## Methods
▪ Input data
▪ technical details of CHP operation
Fuel | [7 empty] | Electricity | [5 empty] | Condensate
Calorific value |  |  |  | CV | 7000 | kg/Gcal |  | Production |  |  | E | 80 | MWh | LP1 Condensate Enthalpy |  | Hl1c | 0.435 | kJ/kg
[8 empty] | Auxilary Service |  |  | Eaux | 3 | MWh | LP1 Condensate Eltropy |  | Sl1c | 1.36 | kJ/kgK
Steam Boiler (HP - high pressure) | [13 empty] | LP2 Condensate Enthalpy |  | Hl2c | 0.373 | kJ/kg
Efficiency |  |  |  | η_boiler | 0.92 |  |  | Medium pressure steam (15 ata, industrial steam) | [5 empty] | LP2 Condensate Eltropy |  | Sl2c | 1.18 | kJ/kgK
HP Steam Production |  |  |  | Q0 | 517 | t/h |  | MP Steam Production |  |  | Gm | 200 | t/h | MP Condensate Enthalpy |  | Hmc | 0.419 | kJ/kg
HP Enthalpy |  |  |  | Hhp | 3.484 | kJ/t |  | MP Temperature |  |  | tm | 191 | C | MP Condensate Eltropy |  | Smc | 1.3 | kJ/kgK
HP Condensate Enthalpy |  |  |  | Hhpc | 2.387 | kJ/t |  | MP Enthalpy |  |  | Hm | 3.015 | kJ/kg
[8 empty] | MP Eltropy |  |  | Sm | 6.9 | kJ/kgK | Feed Water Consumption |  | Dfw | 517 | t/h
Water | [13 empty] | Feed Water Temperature |  | tfw | 229 | C
Consumption |  |  |  | G | 1618 | t/h |  | Low pressure steam (1,2 ata, LP1) | [5 empty] | Feed Water Enthalpy |  | Hfw | 0.959 | kJ/t
Back Water Temperature |  |  |  | tbw | 53 | C |  | LP1 Steam production |  |  | Gl1 | 57.7 | t/h
Back Water Enthalpy |  |  |  | Hbw | 0.222 | kJ/t |  | LP1 Temperature |  |  | tт1 | 104 | C | Convert Coefficients
After Heat Exchange #2 | [7 empty] | LP1 Enthalpy |  |  | Hт1 | 2.613 | kJ/kg | 1 W = 3600 J/h |  |  | 0.27778 | MWh/GJ
Water Temperature |  |  |  | thx2 | 83.5 | C |  | LP1 Eltropy |  |  | Sт1 | 7.12 | kJ/kgK | 1 ton of univ. fuel = 8,14 MWh |  |  | 0.12285 | tuf/MWh
Water Enthalpy |  |  |  | Hhx2 | 0.35 | kJ/t
After Heat Exchange #1 | [7 empty] | Low pressure steam (0,7 ata, LP2) | [5 empty] | Steam bus and Water Boiler
Water Temperature |  |  |  | thx1 | 102 | C |  | LP2 Steam Production |  |  | Gl2 | 96.2 | t/h | HP Steam Bus Efficiency |  | η0 | 100 | %
Water Enthalpy |  |  |  | Hhx1 | 0.427 | kJ/t |  | LP2 Temperature |  |  | tl2 | 89 | C | Heat Water Boiler Efficiency |  | η_wboiler | 0.93
Forward Water Temperature |  |  |  | tfw | 130 | C |  | LP2 Enthalpy |  |  | Hl2 | 2.546 | kJ/kg | Heat Echange Effifciency |  | η_hx1,2 | 1 | %
Forward Water Enthalpy |  |  |  | Hfw | 0.544 | kJ/t |  | LP2 Eltropy |  |  | Sl2 | 7.16 | kJ/kgK | Outside Temperature |  | t_out | 20 | C
▪ market data
Equivalent Fuel Price |  |  |  | Zf | 100 | EUR/tef
▪ CHP load calculation | [8 empty] | ▪ Variables and Notations
Coefficients (and method where it's used)
Turbine Qm load (industrial steam) | [8 empty] | Qe | HP Steam consumption for Electrcty production (net production) | [7 empty] | Exergy method (section. 2.2.2)
Qm = Gm * (Hm - Hmc) | [17 empty] | γm | Exergy Temperature Function for MP Steam
Qm |  | 519.2 | GJ | 144.2222 | MWh | 124.0088 | Gcal |  | Q0m | HP Steam consumption for MP Steam proction | [7 empty] | γl1 | Exergy Temperature Function for LP1 Steam
[9 empty] | Q0l | HP Steam consumption for LP Steam proction (Ql1 + Ql2) | [7 empty] | γl2 | Exergy Temperature Function for LP2 Steam
Turbine Ql1 load (1,2 ata) | [8 empty] | dQe | Additional HP Steam consumption for Electricity production (in ORGRES methon only)
Ql1 = Gl1 * (Hl1 - Hl1c) | [17 empty] | Proportional distribution method by ORGRES (secion. 2.2.3)
Ql1 |  | 125.6706 | GJ | 34.9085 | MWh | 30.0159 | Gcal | [10 empty] | γm | MP Steam coefficient
[9 empty] | Be | Equivalent Fuel consumption for Electricity production (net production) | [7 empty] | γl1 | LP1 Steam coefficient
Turbine Ql2 load (0,7 ata) | [8 empty] | Bm | Equivalent Fuel consumption for MP Steam production | [7 empty] | γl2 | LP2 Steam coefficient
Ql2 = Gl2 * (Hl2 - Hl2c) | [8 empty] | Bl | Equivalent Fuel consumption for LP Steam production (Ql1 + Ql2) | [7 empty] | γdqe | Additional Fuel consumption for Electricity production
Ql2 |  | 209.0426 | GJ | 58.0674 | MWh | 49.929 | Gcal |  | Bml | Equivalent Fuel consumption for both MP and LP Steam production | [7 empty] | γml | MP and LP Steam coefficient
[9 empty] | Bl1 | Equivalent Fuel consumption for LP1 Steam production
Total Turbine Ql load (Ql1 + Ql2) | [8 empty] | Bl2 | Equivalent Fuel consumption for LP2 Steam production | [7 empty] | Work method (section. 2.2.4)
Ql = Ql1 + Ql2 | [8 empty] | Bl3 | Water Boiler Equivalent Fuel consumption for Ql3 production | [7 empty] | γml | Coefficient Bm/Bl
Ql |  | 334.7132 | GJ | 92.9759 | MWh | 79.9449 | Gcal |  | Bl_total | Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Steam parameters consideration method (section. 2.2.5)
Steam Boiler Q0 load | [17 empty] | γe | Electricity coefficient
Q0 = Ghp * (Hhp - Hhpc) | [8 empty] | be | Electricuty Fuel Rate (per 1 MWh) | [7 empty] | γBm | MP Steam coefficient
Q0 |  | 1305.425 | GJ | 362.6181 | MWh | 311.7954 | Gcal |  | bm | MP Steam Fuel Rate (per 1 MWh) | [7 empty] | γBl1 | LP1 Steam coefficient
[9 empty] | bl | LP (LP1+LP2) Steam Fuel Rate (per 1 MWh) | [7 empty] | γBl2 | LP2 Steam coefficient
Steam Boiler fuel consumption | [8 empty] | bml | Both LP and MP Steam Fuel Rate (per 1 MWh)
Bsb = Q0/η_boiler | [8 empty] | bl1 | LP1 Steam Fuel Rate (per 1 MWh) | [7 empty] | Energy method (section. 2.3.3)
Bsb |  | 1418.9402 | GJ | 394.1501 | MWh | 48.4214 | tef |  | bl2 | LP2 Steam Fuel Rate (per 1 MWh) | [7 empty] | γe | Electricity-to-heat coefficient
[9 empty] | bl3 | Water Boiler Heat Fuel Rate (per 1 MWh) | [7 empty] | γm | Electricity-to-steam coefficient
Water Boiler load | [8 empty] | bl_total | Total Heat Fuel Rate | [7 empty] | γl | Electricity-to-heat coefficient
Ql3 = G * (Hfw - Hhx1) | [8 empty] | dbml | Additional reduction of Bml for LP and MP Steams (method ORGRES only)
Ql3 |  | 189.306 | GJ | 52.585 | MWh | 45.215 | Gcal | [10 empty] | Method of an alternative way of electricity supply (section. 2.3.5)
[18 empty] | γe | Power-to-Energy coefficient
Расход топлива водогрейным котлом | [8 empty] | Em | MP Exergy | [7 empty] | γml | ML and LP Steam-to-Energy coefficient
Bwb = Ql3/η_wboiler | [8 empty] | El1 | LP1 Exergy | [7 empty] | γl | Coefficient Ql/total heat
Bwb |  | 203.5548 | GJ | 56.543 | MWh | 6.9463 | tef |  | El2 | LP2 Exergy
[9 empty] | Ee | Electricity Exergy | [7 empty] | Benefit distribution method (section. 2.3.6)
[9 empty] | E_total | Total Exergy | [7 empty] | ηe | Turbine Efficiency with Electricity production only (Condensate mode)
[9 empty] | if variable is marked with quote (') the variable refers to intermediate result | [8 empty] | New! Method based on the linear steam turbine characteristic curve (section. 3)
[18 empty] | a1, a2, a3, a0 | Linear Coefficients for Steam Characteristic Curve
Warning! In the paper Electricity is indexed with N but here, in the file, E letter is used.
▪ Calculation of fuel rates and products cost
"Physical" method (section. 2.2.1)
Input Data |  |  |  | What to calculate?
Q0 | 362.6181 | MWh |  | HP Steam consumption for Electrcty production (net production)
Qm | 144.2222 | MWh |  | Qe = Q0 - (Qm + Ql)
Ql | 92.9759 | MWh |  | Qe | 125.4199 | MWh
Ql3 | 52.585 | MWh |  | Equivalent Fuel consumption for Electricity production (net production)
Be = Qe/Q0*Bsb
η_boiler | 92% |  |  | Be | 16.7477 | tef
Electricuty Fuel Rate (per 1 MWh)
E | 80 | MWh |  | be = Be/(E-Eaux)
Eaux | 3 | MWh |  | be | 0.2175 | tef/MWh |  | 217.5022 | kgef/MWh |  | 21.7502 | EUR/MWh
Equivalent Fuel consumption for MP Steam production
Bwb | 6.9463 | tef |  | Bm = Qm/Q0*Bsb
Bsb | 48.4214 | tef |  | Bm | 19.2584 | tef
MP Steam Fuel Rate (per 1 MWh)
Zf | 100 | EUR/tef |  | bm = Bm/Qm
|  |  |  | bm | 0.13353 | tef/MWh |  | 133.5327 | kgef/MWh |  | 13.3533 | EUR/MWh
Equivalent Fuel consumption for LP Steam production (Ql1 + Ql2)
Bl = Ql/Q0*Bsb
|  |  |  | Bl | 12.4153 | tef
LP (LP1+LP2) Steam Fuel Rate (per 1 MWh)
bl = Bl/Ql
|  |  |  | bl | 0.13353 | tef/MWh |  | 133.5327 | kgef/MWh |  | 13.3533 | EUR/MWh
Water Boiler Heat Fuel Rate (per 1 MWh)
bl3 = Bwb/Ql3
|  |  |  | bl3 | 0.1321 | tef/MWh |  | 132.0969 | kgef/MWh |  | 13.2097 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Bl + Bwb
|  |  |  | Bl_total | 19.3616 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql + Ql3)
|  |  |  | bl_total | 0.13301 | tef/MWh |  | 133.014 | kgef/MWh |  | 13.3014 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 30.25% | 34.59% | 217.5022 |  | 21.7502
Industrial steam |  |  | 34.78% | 39.77% | 133.5327 |  | 13.3533
Heat |  |  | 34.97% | 25.64% | 133.014 | 133.5327 | 13.3014 | 13.3533
IMPORTANT: results reflect nonconsitency
1) Method doesn't correspond to the Second Thermodynamic Law
2) CHP Heat Fuel Rate in combined operation mode is higher than Heat Fuel Rate for Water Boiler only. This is nonsense!
Exergy method (section. 2.2.2)
Input Data |  |  |  | What to calculate?
T | 293 | K |  | Heat Flow Function (see paper) provides temperatures tm, tl1, tl2
tm | 191 | C |  | Exergy Temperature Function for MP Steam
tl1 | 104 | C |  | γm = 1 - (Temp. env.(K) / tm (K))
tl2 | 89 | C |  | γm | 0.36853
Exergy Temperature Function for LP1 Steam
Qm | 144.2222 | MWh |  | γl1 = 1 - (Temp. env.(K) / tl1 (K))
Ql1 | 34.9085 | MWh |  | γl1 | 0.22281
Ql2 | 58.0674 | MWh |  | Exergy Temperature Function for LP2 Steam
Ql3 | 52.585 | MWh |  | γl2 = 1 - (Temp. env.(K) / tl2 (K))
|  |  |  | γl2 | 0.19061
E | 80 | MWh |  | MP Exergy
Eaux | 3 | MWh |  | Em = Qm * γm
|  |  |  | Em | 53.1509 | MWh
Bsb | 48.4214 | tef |  | LP1 Exergy
Bwb | 6.9463 | tef |  | El1 = Ql1 * γl1
|  |  |  | El1 | 7.778 | MWh
Zf | 100 | EUR/tef |  | LP2 Exergy
El2 = Ql2 * γl2
|  |  |  | El2 | 11.0681 | MWh
Electricity Exergy
Ee = E
|  |  |  | Ee | 80 | MWh
Total Exergy
E_total = Ee + Em + El1 + El2
|  |  |  | E_total | 151.997 | MWh
Equivalent Fuel consumption for MP Steam production
Bm = Bsb * Em / E_total
|  |  |  | Bm | 16.9322 | tef
MP Steam Fuel Rate (per 1 MWh)
bm = Bm/Qm
|  |  |  | bm | 0.1174 | tef/MWh |  | 117.4033 | kgef/MWh |  | 11.7403 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl = Bsb * (El1 + El2) / E_total
|  |  |  | Bl | 6.0038 | tef
LP1 Steam Fuel Rate (per 1 MWh)
bl = Bl/Ql
|  |  |  | bl | 0.064573 | tef/MWh |  | 64.5734 | kgef/MWh |  | 6.4573 | EUR/MWh
Equivalent Fuel consumption for Electricity production (net production)
Be = Bsb * Ee / E_total
|  |  |  | Be | 25.4854 | tef
Electricuty Fuel Rate (per 1 MWh)
be = Be/(E-Eaux)
|  |  |  | be | 0.33098 | tef/MWh |  | 330.9798 | kgef/MWh |  | 33.098 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Bl + Bwb
|  |  |  | Bl_total | 12.9501 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql + Ql3)
|  |  |  | bl_total | 0.088967 | tef/MWh |  | 88.9668 | kgef/MWh |  | 8.8967 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 46.03% | 52.63% | 330.9798 |  | 33.098
Industrial steam |  |  | 30.58% | 34.97% | 117.4033 |  | 11.7403
Heat |  |  | 23.39% | 12.4% | 88.9668 | 64.5734 | 8.8967 | 6.4573
NOTE: nowadays, this is the most widely aplied method for combined heat and power production
Proportional distribution method by ORGRES (secion. 2.2.3)
Input Data |  |  |  | What to calculate?
Special coefficient for Turbine which operates with 130 ata preassure
k | 0.4
HP Steam consumption for Electrcty production (net production)
Q0 | 362.6181 | MWh |  | Qe = Q0 - (Qm + Ql1 + Ql2)
Qm | 144.2222 | MWh |  | Qe | 125.4199 | MWh
Ql1 | 34.9085 | MWh |  | MP Steam coefficient
Ql2 | 58.0674 | MWh |  | γm = (Hm - Нhpc) / (Нhp - Нhpc) * (1 + k * (Hhp - Нm) / (Нhp - Нhpc))
Ql3 | 52.585 | MWh |  | γm | 0.67037
LP1 Steam coefficient
γl1 = (Hl1 - Нhpc) / (Нhp - Нhpc) * (1 + k * (Нhp - Hl1 ) / (Нph - Нhpc))
Нhp | 3.484 | kJ/t |  | γl1 | 0.27145
Нm | 3.015 | kJ/t |  | LP2 Steam coefficient
Нl1 | 2.613 | kJ/t |  | γl2 = (Hl2 - Нhpc) / (Нhp - Нhpc) * (1 + k * (Нhp - Hl2) / (Нhp - Нhpc))
Нl2 | 2.546 | kJ/t |  | γl2 | 0.19451
Нhpc | 2.387 | kJ/t |  | Additional HP Steam consumption for Electricity production (in ORGRES methon only)
dQe = Qm * (1-γп) + Ql1 * (1-γт1) + Ql2 * (1-γт2)
Bsb | 48.4214 | tef |  | dQe | 119.7452 | MWh
Bwb | 6.9463 | tef |  | Additional Fuel consumption for Electricity production
γdqe = (Qe + dQe)/(Qe + dQe + Qm + Ql1 + Ql2)
E | 80 | MWh |  | γdqe | 0.50826
Eaux | 3 | MWh |  | Equivalent Fuel consumption for Electricity production (net production)
Be = Bsb * γdqe
Zf | 100 | EUR/tef |  | Be | 24.6106 | tef
Electricuty Fuel Rate (per 1 MWh)
be = Be / (E - Eaux)
|  |  |  | be | 0.31962 | tef/MWh |  | 319.6178 | kgef/MWh |  | 31.9618 | EUR/MWh
Equivalent Fuel consumption for both MP and LP Steam production
Bml = B - Be
|  |  |  | Bml | 23.8108 | tef
Both LP and MP Steam Fuel Rate (per 1 MWh)
bml = Bml/(Qm + Ql1 + Ql2)
|  |  |  | bml | 0.10038 | tef/MWh
MP and LP Steam coefficient
γml = (Qe + dQe + Qm + Ql1 + Ql2)/(Qe + Qm + Ql1 + Ql2)
|  |  |  | γml | 1.3302
Fuel rate bml adjustment
bml_adj = bml * γml
|  |  |  | bml_adj | 0.13353 | tef/MWh
Mean value of steams coefficients
γml_mean = (Qm* γm + Ql1 * γl1 + Ql2 * γl2)/(Qm + Ql1 + Ql2)
|  |  |  | γml_mean | 0.49517
Additional reduction of Bml for LP and MP Steams (method ORGRES only)
dbml = bml_adj - bml
|  |  |  | dbml | 0.033149 | tef/MWh
Distribution by steams
1) Quota of dbml for MP steam
dbml(MP) = dbml * (1- γm)/(1-γml_mean)
|  |  |  | dbml(MP) |  | 0.021645 | tef/MWh
2) Quota of dbml for LP1 steam
dbml(LP1) = dbml * (1- γl1)/(1-γml_mean)
|  |  |  | dbml(LP1) |  | 0.047839 | tef/MWh
3) Quota of dbml for LP2 steam
dbml(LP2) = dbml * (1- γl2)/(1-γml_mean)
|  |  |  | dbml(LP2) |  | 0.052891 | tef/MWh
MP Steam Fuel Rate (per 1 MWh)
bm = bml_adj - dbml(MP)
|  |  |  | bm | 0.11189 | tef/MWh |  | 111.888 | kgef/MWh |  | 11.1888 | EUR/MWh
LP1 Steam Fuel Rate (per 1 MWh)
bl1 = bml_adj - dbml(LP1)
|  |  |  | bl1 | 0.085693 | tef/MWh |  | 85.6932 | kgef/MWh
LP2 Steam Fuel Rate (per 1 MWh)
bl2 = bml_adj - dbml(LP2)
|  |  |  | bl2 | 0.080642 | tef/MWh |  | 80.6416 | kgef/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
bl = (Ql1 * bl1 + Ql2 * bl2)/(Ql1 + Ql2)
|  |  |  | bl | 0.082538 | tef/MWh |  | 82.5383 | kgef/MWh |  | 8.2538 | EUR/MWh
Equivalent Fuel consumption for MP Steam production
Bm = bm * Qm
|  |  |  | Bm | 16.1367 | tef
Equivalent Fuel consumption for LP Steam production (Ql1 + Ql2)
Bl = bl * (Ql1 + Ql2)
|  |  |  | Bl | 7.6741 | tef
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Bl + Bwb
|  |  |  | Bl_total | 14.6204 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql1 + Ql2 + Ql3)
|  |  |  | bl_total | 0.10044 |  |  | 100.4417 | kgef/MWh |  | 10.0442 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 44.45% | 50.83% | 319.6178 |  | 31.9618
Industrial steam |  |  | 29.14% | 33.33% | 111.888 |  | 11.1888
Heat |  |  | 26.41% | 15.85% | 100.4417 | 82.5383 | 10.0442 | 8.2538
NOTE: Don't ever use that method. Looks like dull jungling!
1) This is the most cumbersome methoed of all.
Work method (section. 2.2.4)
Input Data |  |  |  | What to calculate?
*** NOTE: Here additional point of ST-135 characteristic curve are used for Q0 = 362,6 MWh ***
Q0 | 362.6181 | MWh
Econd | 139 | MWh | Turbine operation mode (condensational): Qm = Ql1 = Ql2 = 0
El | 122.5 | MWh | Turbine operation mode: Qm = 0; Ql1 = 34,9 MW, Ql2 = 58,1 MW
Em (see note above) | 96.5 | MWh | Turbine operation mode Ql1 = Ql2 = 0; Qm = 144,2 MW
Em | 82.5553 | MWh
Equivalent Fuel consumption for Electricity production (net production)
Qm | 144.2222 | MWh |  | Be = Bsb * E / Econd
Ql1 | 34.9085 | MWh |  | Be | 27.8684 | tef
Ql2 | 58.0674 | MWh |  | Electricuty Fuel Rate (per 1 MWh)
Ql3 | 52.585 | MWh |  | be = Be / (E - Eaux)
|  |  |  | be | 0.36193 | tef/MWh |  | 361.9276 | kgef/MWh |  | 36.1928 | EUR/MWh
E | 80 | MWh |  | Equivalent Fuel consumption for both MP and LP Steam production
Eaux | 3 | MWh |  | Bml = B - Be
|  |  |  | Bml | 20.553 | tef
Bsb | 48.4214 | tef |  | Both LP and MP Steam Fuel Rate (per 1 MWh)
Bwb | 6.9463 | tef |  | bml = Bml/(Qm + Ql1 + Ql2)
|  |  |  | bml | 0.086649 | tef/MWh
Zf | 100 | EUR/tef |  | Coefficient Bm/Bl
γml = Bm/Bl = (Econd - El)/(Econd - Em)
|  |  |  | γml | 3.4209
Equivalent Fuel consumption for MP Steam production
Bm = Bmт / (1+1/γml)
|  |  |  | Bm | 15.9039 | tef
MP Steam Fuel Rate (per 1 MWh)
bm = Bm/Qm
|  |  |  | bm | 0.11027 | tef/MWh |  | 110.2736 | kgef/MWh |  | 11.0274 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl = Bm / γml
|  |  |  | Bl | 4.6491 | tef
LP (LP1+LP2) Steam Fuel Rate (per 1 MWh)
bl = Bl/(Ql1 +Ql2)
|  |  |  | bl | 0.050003 | tef/MWh |  | 50.0028 | kgef/MWh |  | 5.0003 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Вl + Bwb
|  |  |  | Bl_total | 11.5954 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql1 + Ql2 + Ql3)
|  |  |  | bl_total | 0.07966 |  |  | 79.6599 | kgef/MWh |  | 7.966 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 50.33% | 57.55% | 361.9276 |  | 36.1928
Industrial steam |  |  | 28.72% | 32.84% | 110.2736 |  | 5.0003
Heat |  |  | 20.94% | 9.601% | 79.6599 | 50.0028 | 7.966 | 5.0003
Steam parameters consideration method (section. 2.2.5)
Input Data |  |  |  | What to calculate?
*** Steam coefficients are taken from ORGRES method ***
γm | 0.67037 |  |  | Electricity coefficient
γl1 | 0.27145 |  |  | γe = (Q0 - (Qm*γm + Ql1*γl1 + Ql2*γl2))/Q0
γl2 | 0.19451 |  |  | γe | 0.6761
Equivalent Fuel consumption for Electricity production (net production)
Q0 | 362.6181 | MWh |  | Be = Bsb * γe
Qm | 144.2222 | MWh |  | Be | 32.7376 | tef
Ql1 | 34.9085 | MWh |  | Electricuty Fuel Rate (per 1 MWh)
Ql2 | 58.0674 | MWh |  | be = Be / (E-Eaux)
Ql3 | 52.585 | MWh |  | be | 0.42516 | tef/MWh |  | 425.1634 | kgef/MWh |  | 42.5163 | EUR/MWh
Equivalent Fuel consumption for both MP and LP Steam production
Bsb | 48.4214 | tef |  | Bml = B - Be
Bwb | 6.9463 | tef |  | Bml | 15.6838 | tef
MP Steam coefficient
E | 80 | MWh |  | γBm = γm*Qm/(γm*Qm + γl1*Ql1 + γl2*Ql2)
Eaux | 3 | MWh |  | γBm | 0.82316
LP1 Steam coefficient
Zf | 100 | EUR/tef |  | γBl1 = γl1*Ql1/(γm*Qm + γl1*Ql1 + γl2*Ql2)
|  |  |  | γBl1 | 0.080677
LP2 Steam coefficient
γBl2 = γl2*Ql2/(γm*Qm + γl1*Ql1 + γl2*Ql2)
|  |  |  | γBl2 | 0.096166
Equivalent Fuel consumption for MP Steam production
Bm = Bml * γBm
|  |  |  | Bm | 12.9102 | tef
MP Steam Fuel Rate (per 1 MWh)
bm = Bm / Qm
|  |  |  | bm | 0.089516 | tef/MWh |  | 89.5163 | kgef/MWh |  | 8.9516 | EUR/MWh
Equivalent Fuel consumption for LP Steam production (Ql1 + Ql2)
Bl = Bml * (γBl1 + γBl2)
|  |  |  | Bl | 2.7736 | tef
LP (LP1+LP2) Steam Fuel Rate (per 1 MWh)
bl = Bl / (Ql1 + Ql2)
|  |  |  | bl | 0.029831 | tef/MWh |  | 29.831 | kgef/MWh |  | 2.9831 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Вl + Bwb
|  |  |  | Bl_total | 9.7199 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql1 + Ql2 + Ql3)
|  |  |  | bl_total | 0.066775 |  |  | 66.7754 | kgef/MWh |  | 6.6775 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 59.13% | 67.61% | 425.1634 |  | 42.5163
Industrial steam |  |  | 23.32% | 26.66% | 89.5163 |  | 8.9516
Heat |  |  | 17.56% | 5.728% | 66.7754 | 29.831 | 6.6775 | 2.9831
Energy method (section. 2.3.3)
Input Data |  |  |  | What to calculate?
Qm | 144.2222 | MWh |  | Electricity-to-heat coefficient
Ql | 92.9759 | MWh |  | γe = E/(E + Qm + Ql)
Ql3 | 52.585 | MWh |  | γe | 0.25221
Electricity-to-steam coefficient
Bsb | 48.4214 | tef |  | γm = Qm/(E + Qm + Ql)
Bwb | 6.9463 | tef |  | γm | 0.45468
Electricity-to-heat coefficient
E | 80 | MWh |  | γl = Ql/(N + Qm + Ql)
Eaux | 3 | MWh |  | γl | 0.29312
Equivalent Fuel consumption for Electricity production (net production)
Zf | 100 | EUR/tef |  | Be = γe * Bsb
|  |  |  | Be | 12.2123 | tef
Equivalent Fuel consumption for MP Steam production
Bm = γm * Bsb
|  |  |  | Bm | 22.016 | tef
Equivalent Fuel consumption for LP Steam production (Ql1 + Ql2)
Bl = γl * Bsb
|  |  |  | Bl | 14.1931 | tef
Electricuty Fuel Rate (per 1 MWh)
be = Be/(E - Eaux)
|  |  |  | be | 0.1586 | tef/MWh |  | 158.601 | kgef/MWh |  | 15.8601 | EUR/MWh
MP Steam Fuel Rate (per 1 MWh)
bm = Bm/Qm
|  |  |  | bm | 0.15265 | tef/MWh |  | 152.6534 | kgef/MWh |  | 15.2653 | EUR/MWh
LP (LP1+LP2) Steam Fuel Rate (per 1 MWh)
bl = Bl/Ql
|  |  |  | bl | 0.15265 | tef/MWh |  | 152.6534 | kgef/MWh |  | 15.2653 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Bl + Bwb
|  |  |  | Bl_total | 21.1394 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql + Ql3)
|  |  |  | bl_total | 0.14523 | tef/MWh |  | 145.2272 | kgef/MWh |  | 14.5227 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 22.06% | 25.22% | 158.601 |  | 15.8601
Industrial steam |  |  | 38.18% | 45.47% | 152.6534 |  | 15.2653
Heat |  |  | 39.76% | 29.31% | 145.2272 | 152.6534 | 15.2653 | 14.5227
NOTE: the method is too simple tp consider details of combined power and heat production
1) This method should be put in economic group of cost allocation methods.
Work method (section. 2.3.2)
Input Data |  |  |  | What to calculate?
NOTE: See method on under-produced electricity (#4)
Exergy method (section.2.3.1)
Input Data |  |  |  | What to calculate?
NOTE: See exergy method above
Method of an alternative way of heat supply (section.2.3.4)
Input Data |  |  |  | What to calculate?
Qm | 144.2222 | MWh |  | Equivalent Fuel consumption for LP Steam production (Ql1 + Ql2)
Ql | 92.9759 | MWh |  | Bl = Ql / η_wboiler
Ql3 | 52.585 | MWh |  | Bl | 99.9741 | MWh |  | 12.2818 | tef
LP (LP1+LP2) Steam Fuel Rate (per 1 MWh)
η_wboiler | 93% |  |  | bl = Bl/Ql
η_boiler | 92% |  |  | bl | 0.1321 | tef/MWh |  | 132.0969 | kgef/MWh |  | 13.2097 | EUR/MWh
Equivalent Fuel consumption for MP Steam production
Bsb | 48.4214 | tef |  | Bm = Qm / η_boiler
Bwb | 6.9463 | tef |  | Bm | 156.7633 | MWh |  | 19.2584 | tef
MP Steam Fuel Rate (per 1 MWh)
E | 80 | MWh |  | bm = Bm/Qm
Eaux | 3 | MWh |  | bm | 0.13353 | tef/MWh |  | 133.5327 | kgef/MWh |  | 13.3533 | EUR/MWh
Equivalent Fuel consumption for Electricity production (net production)
Zf | 100 | EUR/tef |  | Be = Вsb - Вm - Bl
|  |  |  | Be | 16.8812 | tef
Electricuty Fuel Rate (per 1 MWh)
be = Bе/(E-Eaux)
|  |  |  | be | 0.21924 | tef/MWh |  | 219.2359 | kgef/MWh |  | 21.9236 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Bl + Bwb
|  |  |  | Bl_total | 19.2281 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql + Ql3)
|  |  |  | bl_total | 0.1321 | tef/MWh |  | 132.0969 | kgef/MWh |  | 13.2097 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 30.49% | 34.86% | 219.2359 |  | 21.9236
Industrial steam |  |  | 34.78% | 39.77% | 133.5327 |  | 13.3533
Heat |  |  | 34.73% | 25.36% | 132.0969 | 132.0969 | 13.2097 | 13.2097
NOTE: Very straightforward economic method
Method of an alternative way of electricity supply (section. 2.3.5)
Input Data |  |  |  | What to calculate?
Qm | 144.2222 | MWh |  | Power-to-Energy coefficient
Ql | 92.9759 | MWh |  | γe = Q0 (Nконд) / Q0
Ql3 | 52.585 | MWh |  | γe | 0.67184
ML and LP Steam-to-Energy coefficient
Q0 (Econd) | 243.6216 | MWh |  | γml = (Q0 - Q0(Econd))/Q0
Q0 | 362.6181 | MWh |  | γml | 0.32816
Equivalent Fuel consumption for Electricity production (net production)
Bsb | 48.4214 | tef |  | Be = γe * Bsb
Bwb | 6.9463 | tef |  | Be | 32.5315 | tef
Electricuty Fuel Rate (per 1 MWh)
E = Econd | 80 | MWh |  | be = Bе/(E-Eaux)
Eaux | 3 | MWh |  | be | 0.42249 | tef/MWh |  | 422.4865 | kgef/MWh |  | 42.2487 | EUR/MWh
Equivalent Fuel consumption for both MP and LP Steam production
Zf | 100 | EUR/tef |  | Bml = γml * Bsb
|  |  |  | Bml | 15.8899 | tef
ML and LP Steam-to-Energy coefficient
γml = Qm/(Qm + Ql)
|  |  |  | γml | 0.60802
Coefficient Ql/total heat
γl = Ql/(Qm + Ql)
|  |  |  | γl | 0.39198
Equivalent Fuel consumption for MP Steam production
Bm = γm * Bml
|  |  |  | Bm | 9.6615 | tef
Equivalent Fuel consumption for LP Steam production (Ql1 + Ql2)
Bl = γl * Bml
|  |  |  | Bl | 6.2285 | tef
MP Steam Fuel Rate (per 1 MWh)
bm = Bm/Qm
|  |  |  | bm | 0.06699 | tef/MWh |  | 66.9901 | kgef/MWh |  | 6.699 | EUR/MWh
LP (LP1+LP2) Steam Fuel Rate (per 1 MWh)
bl = Bl/Ql
|  |  |  | bl | 0.06699 | tef/MWh |  | 66.9901 | kgef/MWh |  | 6.699 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Bl + Bwb
|  |  |  | Bl_total | 13.1748 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql + Ql3)
|  |  |  | bl_total | 0.09051 | tef/MWh |  | 90.5104 | kgef/MWh |  | 9.051 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 58.76% | 67.18% | 422.4865 |  | 42.2487
Industrial steam |  |  | 17.45% | 19.95% | 66.9901 |  | 6.699
Heat |  |  | 23.8% | 12.86% | 90.5104 | 66.9901 | 9.051 | 6.699
Benefit distribution method (section. 2.3.6)
Input Data |  |  |  | What to calculate?
Qm | 144.2222 | MWh |  | Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Ql | 92.9759 | MWh |  | Bl' = Ql / η_wboiler
Ql3 | 52.585 | MWh |  | Bl' | 12.2818 | tef
Equivalent Fuel consumption for MP Steam production
η_wboiler | 93% |  |  | Bm' = Qm / η_boiler
η_boiler | 92% |  |  | Bm' | 19.2584 | tef
Turbine Efficiency with Electricity production only (Condensate mode)
Q0 (Econd) | 243.6216 | MWh |  | ηe = Econd / Q0(Econd) / η_boiler
|  |  |  | ηe | 0.35693
Bsb | 48.4214 | tef |  | Equivalent Fuel consumption for Electricity production (net production)
Bwb | 6.9463 | tef |  | Be' = E / ηe
|  |  |  | Be' | 27.5346 | tef
E = Econd | 80 | MWh |  | Steam Boiler fuel consumption
Eaux | 3 | MWh |  | Bsb' = Be' + Bm' + Bl'
|  |  |  | Bsb' | 59.0748 | tef
Zf | 100 | EUR/tef |  | Equivalent Fuel consumption for Electricity production (net production)
Be = Be'/Вsb' * Bsb
|  |  |  | Be | 22.5691 | tef
Equivalent Fuel consumption for MP Steam production
Bm = Bm'/Вsb' * Bsb
|  |  |  | Bm | 15.7854 | tef
Equivalent Fuel consumption for LP Steam production (Ql1 + Ql2)
Bl = Bl'/Вsb' * Bsb
|  |  |  | Bl | 10.0669 | tef
Electricuty Fuel Rate (per 1 MWh)
be = Bе/(E-Eaux)
|  |  |  | be | 0.2931 | tef/MWh |  | 293.1049 | kgef/MWh |  | 29.3105 | EUR/MWh
MP Steam Fuel Rate (per 1 MWh)
bm = Bm/Qm
|  |  |  | bm | 0.10945 | tef/MWh |  | 109.4517 | kgef/MWh |  | 10.9452 | EUR/MWh
LP (LP1+LP2) Steam Fuel Rate (per 1 MWh)
bl = Bl/Ql
|  |  |  | bl | 0.10827 | tef/MWh |  | 108.2748 | kgef/MWh |  | 10.8275 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Bl + Bwb
|  |  |  | Bl_total | 17.0133 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql + Ql3)
|  |  |  | bl_total | 0.11688 | tef/MWh |  | 116.8807 | kgef/MWh |  | 11.6881 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 40.76% | 46.61% | 293.1049 |  | 29.3105
Industrial steam |  |  | 28.51% | 32.6% | 109.4517 |  | 10.9452
Heat |  |  | 30.73% | 20.79% | 116.8807 | 108.2748 | 11.6881 | 10.8275
Benefit and risk-sharing method (section. 2.3.7)
Input Data |  |  |  | What to calculate?
Fuel rates be, bm, bl are calculated according to alternative heat production method
be | 0.21924 | tef/MWh |  | Equivalent Fuel consumption for MP Steam production
bm | 0.13353 | tef/MWh |  | Bm = bm * Qm
bl | 0.1321 | tef/MWh |  | Bm | 19.2584 | tef
Qm | 144.2222 | MWh |  | Heat fuel rate - to - Electricity fuel rate dependency (considering market price risk)
Ql | 92.9759 | MWh |  | bl_m = ((B - Bm) - be_m * (1+r) * (E - Eaux)) / Ql
Ql3 | 52.585 | MWh
Scenarios
E | 80 | MWh |  | Price change ® |  | bт_m | [7 empty] | be_m * (1+r)
Eaux | 3 | MWh |  | -70% |  | 0.25919 | tef/MWh |  | 259.1924 | kgef/MWh |  | 25.9192 | EUR/MWh | 0.065771 | tef/MWh
|  |  |  | -60% |  | 0.24104 | tef/MWh |  | 241.0359 | kgef/MWh |  | 24.1036 | EUR/MWh | 0.087694 | tef/MWh
Bsb | 48.4214 | tef |  | -50% |  | 0.22288 | tef/MWh |  | 222.8794 | kgef/MWh |  | 22.2879 | EUR/MWh | 0.10962 | tef/MWh
Bwb | 6.9463 | tef |  | -40% |  | 0.20472 | tef/MWh |  | 204.7229 | kgef/MWh |  | 20.4723 | EUR/MWh | 0.13154 | tef/MWh
|  |  |  | -30% |  | 0.18657 | tef/MWh |  | 186.5664 | kgef/MWh |  | 18.6566 | EUR/MWh | 0.15347 | tef/MWh
be_m | 0.21924 | tef/MWh |  | -20% |  | 0.16841 | tef/MWh |  | 168.4099 | kgef/MWh |  | 16.841 | EUR/MWh | 0.17539 | tef/MWh
|  |  |  | -10% |  | 0.15025 | tef/MWh |  | 150.2534 | kgef/MWh |  | 15.0253 | EUR/MWh | 0.19731 | tef/MWh
Zf | 100 | EUR/tef |  | 0% |  | 0.1321 | tef/MWh |  | 132.0969 | kgef/MWh |  | 13.2097 | EUR/MWh | 0.21924 | tef/MWh
|  |  |  | 10% |  | 0.11394 | tef/MWh |  | 113.9404 | kgef/MWh |  | 11.394 | EUR/MWh | 0.24116 | tef/MWh
|  |  |  | 20% |  | 0.095784 | tef/MWh |  | 95.7839 | kgef/MWh |  | 9.5784 | EUR/MWh | 0.26308 | tef/MWh
|  |  |  | 30% |  | 0.077627 | tef/MWh |  | 77.6274 | kgef/MWh |  | 7.7627 | EUR/MWh | 0.28501 | tef/MWh
|  |  |  | 40% |  | 0.059471 | tef/MWh |  | 59.4709 | kgef/MWh |  | 5.9471 | EUR/MWh | 0.30693 | tef/MWh
|  |  |  | 50% |  | 0.041314 | tef/MWh |  | 41.3144 | kgef/MWh |  | 4.1314 | EUR/MWh | 0.32885 | tef/MWh
|  |  |  | 60% |  | 0.023158 | tef/MWh |  | 23.1579 | kgef/MWh |  | 2.3158 | EUR/MWh | 0.35078 | tef/MWh
|  |  |  | 70% |  | 0.0050014 | tef/MWh |  | 5.0014 | kgef/MWh |  | 0.50014 | EUR/MWh | 0.3727 | tef/MWh
Equivalent Fuel consumption for Electricity production (net production)
Be = be * (E-Eaux)
|  |  |  | Be | 18.5693 | tef
Equivalent Fuel consumption for MP Steam production
Bm = bm * Qm
|  |  |  | Bm | 19.2584 | tef
Equivalent Fuel consumption for LP Steam production (Ql1 + Ql2)
Bl = bl * Ql
|  |  |  | Bl | 10.5937 | tef
MP Steam Fuel Rate (per 1 MWh)
|  |  |  | bm | 0.13353 | tef/MWh |  | 133.5327 | kgef/MWh |  | 13.3533 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Bl + Bwbт
|  |  |  | Bl_total | 17.54 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql + Ql3)
|  |  |  | bl_total | 0.1205 | tef/MWh |  | 120.4996 | kgef/MWh |  | 12.05 | EUR/MWh
For r = 10%
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 33.54% | 38.35% | 241.1595 |  | 24.116
Industrial steam |  |  | 34.78% | 39.77% | 133.5327 |  | 13.3533
Heat |  |  | 31.68% | 21.88% | 120.4996 | 113.9404 | 12.05 | 11.394
New! Method based on the linear steam turbine characteristic curve (section. 3)
Input data |  |  |  | Calculation
a1 | 1.8492 |  |  | Steam Boiler Q0 load
a2 | 0.71464 |  |  | Q0 = a1 * E + a2 * Qm + a3 * Ql + a0
a3 | 0.28198 |  |  | Q0 | 372.9058 | MWh
a0 | 95.6873 |  |  | HP Steam consumption for Electrcty production (net production)
Qe = a1 * E + a0
Qm | 144.2222 | MWh |  | Qe | 243.6216 | MWh
Ql | 92.9759 | MWh |  | HP Steam consumption for MP Steam proction
Ql3 | 52.585 | MWh |  | Q0m = a2 * Qm
|  |  |  | Q0m | 103.0666 | MWh
Bsb | 48.4214 | tef |  | HP Steam consumption for LP Steam proction (Ql1 + Ql2)
Bwb | 6.9463 | tef |  | Q0l = a3 * Ql
|  |  |  | Q0l | 26.2176 | MWh
E | 80 | MWh |  | Equivalent Fuel consumption for Electricity production (net production)
Eaux | 3 | MWh |  | Be = Qe/Q0*Bsb
|  |  |  | Be | 31.634 | tef
Zf | 100 | EUR/tef |  | Electricuty Fuel Rate (per 1 MWh)
be = Be/(N-Eaux)
|  |  |  | be | 0.41083 | tef/MWh |  | 410.831 | kgef/MWh |  | 41.0831 | EUR/MWh
Equivalent Fuel consumption for MP Steam production
Bm = Q0m/Q0*Bsb
|  |  |  | Bm | 13.3831 | tef
MP Steam Fuel Rate (per 1 MWh)
bп = Bm/Qm
|  |  |  | bm | 0.092795 | tef/MWh |  | 92.7948 | kgef/MWh |  | 9.2795 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bтт = Q0l/Q0*Bsb
|  |  |  | Bl | 3.4043 | tef
LP (LP1+LP2) Steam Fuel Rate (per 1 MWh)
bтт = Bтт/Ql
|  |  |  | bl | 0.036615 | tef/MWh |  | 36.6151 | kgef/MWh |  | 3.6615 | EUR/MWh
Total Equivalent Fuel consumption for Heat production (Ql1 + Ql2 + Ql3)
Bl_total = Bl + Bwb
|  |  |  | Bl_total | 10.3506 | tef
Total Heat Fuel Rate
bl_total = Bl_total/(Ql + Ql3)
|  |  |  | bl_total | 0.071109 | tef/MWh |  | 71.1087 | kgef/MWh |  | 7.1109 | EUR/MWh
CHP product |  |  | Cost, % |  | b, kgef/MWh |  | Fuel Rate, EUR/MWh
|  |  | CHP | Turbine | CHP | Turbine | CHP | Turbine
Electricity |  |  | 57.13% | 65.33% | 410.831 |  | 41.0831
Industrial steam |  |  | 24.17% | 27.64% | 92.7948 |  | 9.2795
Heat |  |  | 18.69% | 7.031% | 71.1087 | 36.6151 | 7.1109 | 3.6615
Note on B283: Irina: This is additional value obtained from ST-135 charateristic curve
Note on B475: Irina: This is additional value obtained from ST-135 charateristic curve
Note on B528: Irina: This is additional value obtained from ST-135 charateristic curve

## Comparison
Table from the paper
Group | № | Method | Fuel rates (for turbine only), tef/MWh |  |  | Fuel cost allocation (for turbime only), %
|  |  | Electricity | Industrial steam | Heat | Electricity | Industrial steam | Heat | For chart
Thermodynamical | 1) | Exergy method (section. 2.2.2) | 0.33098 | 0.1174 | 0.064573 | 52.63% | 34.97% | 12.4% | 0.33098 | 0.1174 | 0.064573 |  |  |  | 52.63% | 34.97% | 12.4%
| 2) | Work method (section. 2.2.4) | 0.36193 | 0.11027 | 0.050003 | 57.55% | 32.84% | 9.601% | 0.36193 | 0.11027 | 0.050003 |  |  |  | 57.55% | 32.84% | 9.601%
| 3) | New! Method based on the linear steam turbine characteristic curve (section. 3) | 0.41083 | 0.092795 | 0.036615 | 65.33% | 27.64% | 7.031% | 0.41083 | 0.092795 | 0.036615 |  |  |  | 65.33% | 27.64% | 7.031%
| 4) | Proportional distribution method by ORGRES (secion. 2.2.3) | 0.31962 | 0.11189 | 0.082538 | 50.83% | 33.33% | 15.85% | 0.31962 | 0.11189 | 0.082538 |  |  |  | 50.83% | 33.33% | 15.85%
| 5) | Steam parameters consideration method (section. 2.2.5) | 0.42516 | 0.089516 | 0.029831 | 67.61% | 26.66% | 5.728% | 0.42516 | 0.089516 | 0.029831 |  |  |  | 67.61% | 26.66% | 5.728%
| 6) | "Physical" method (section. 2.2.1) | 0.2175 | 0.13353 | 0.13301 | 34.59% | 39.77% | 25.64% | 0.2175 | 0.13353 | 0.13301 |  |  |  | 34.59% | 39.77% | 25.64%
Economical | 1) | Benefit and risk-sharing method (section. 2.3.7) | 0.24116 | 0.13353 | 0.11394 | 38.35% | 39.77% | 21.88% |  |  |  | 0.24116 | 0.13353 | 0.11394 |  |  |  | 38.35% | 39.77% | 21.88%
| 2) | Method of an alternative way of heat supply (section.2.3.4) | 0.21924 | 0.13353 | 0.1321 | 34.86% | 39.77% | 25.36% |  |  |  | 0.21924 | 0.13353 | 0.1321 |  |  |  | 34.86% | 39.77% | 25.36%
| 3) | Benefit distribution method (section. 2.3.6) | 0.2931 | 0.10945 | 0.10827 | 46.61% | 32.6% | 20.79% |  |  |  | 0.2931 | 0.10945 | 0.10827 |  |  |  | 46.61% | 32.6% | 20.79%
| 4) | Method of an alternative way of electricity supply (section. 2.3.5) | 0.42249 | 0.06699 | 0.06699 | 67.18% | 19.95% | 12.86% |  |  |  | 0.42249 | 0.06699 | 0.06699 |  |  |  | 67.18% | 19.95% | 12.86%
| 5) | Energy method (section. 2.3.3) | 0.1586 | 0.15265 | 0.15265 | 25.22% | 45.47% | 29.31% |  |  |  | 0.1586 | 0.15265 | 0.15265 |  |  |  | 25.22% | 45.47% | 29.31%
Дополнительная таблица
Group | № | Method | Удельный расход условного топлива на отпуск продуктов с учетом турбины и водогрейного котла, т.у.т./МВт.ч |  |  | Доля расхода условного топлива на выработку продуктов с учетом турбины и водогрейного котла, %
|  |  | Electricity | Industrial steam | Heat | Electricity | Industrial steam | Heat
Thermodynamical | 1 | Exergy method (section. 2.2.2) | 0.33098 | 0.1174 | 0.088967 | 46.03% | 30.58% | 23.39%
| 2 | Work method (section. 2.2.4) | 0.36193 | 0.11027 | 0.07966 | 50.33% | 28.72% | 20.94%
| 3 | New! Method based on the linear steam turbine characteristic curve (section. 3) | 0.41083 | 0.092795 | 0.071109 | 57.13% | 24.17% | 18.69%
| 4 | Proportional distribution method by ORGRES (secion. 2.2.3) | 0.31962 | 0.11189 | 0.10044 | 44.45% | 29.14% | 26.41%
| 5 | Steam parameters consideration method (section. 2.2.5) | 0.42516 | 0.089516 | 0.066775 | 59.13% | 23.32% | 17.56%
| 6 | "Physical" method (section. 2.2.1) | 0.2175 | 0.13353 | 0.13301 | 30.25% | 34.78% | 34.97%
Economical | 1 | Benefit and risk-sharing method (section. 2.3.7) | 0.24116 | 0.13353 | 0.1205 | 33.54% | 34.78% | 31.68%
| 2 | Method of an alternative way of heat supply (section.2.3.4) | 0.21924 | 0.13353 | 0.1321 | 30.49% | 34.78% | 34.73%
| 3 | Benefit distribution method (section. 2.3.6) | 0.2931 | 0.10945 | 0.11688 | 40.76% | 28.51% | 30.73%
| 4 | Method of an alternative way of electricity supply (section. 2.3.5) | 0.42249 | 0.06699 | 0.09051 | 58.76% | 17.45% | 23.8%
| 5 | Energy method (section. 2.3.3) | 0.1586 | 0.15265 | 0.14523 | 22.06% | 38.18% | 39.76%
Данные для треугольника
Group | № | Method | Fuel consumption for Electricity, tef | Fuel consumption for Heat and Industrial Steam production, tef | Bwb | 48.4214 | tef
Thermodynamical | 1 | Exergy method (section. 2.2.2) | 22.2881 | 26.1333
| 2 | Work method (section. 2.2.4) | 24.3721 | 24.0493
| 3 | New! Method based on the linear steam turbine characteristic curve (section. 3) | 27.6653 | 20.7561
| 4 | Proportional distribution method by ORGRES (secion. 2.2.3) | 21.523 | 26.8984
| 5 | Steam parameters consideration method (section. 2.2.5) | 28.6304 | 19.791
| 6 | "Physical" method (section. 2.2.1) | 14.6465 | 33.7748
Economical | 1 | Benefit and risk-sharing method (section. 2.3.7) | 16.2396 | 32.1818
| 2 | Method of an alternative way of heat supply (section.2.3.4) | 14.7633 | 33.6581
| 3 | Benefit distribution method (section. 2.3.6) | 19.7376 | 28.6838
| 4 | Method of an alternative way of electricity supply (section. 2.3.5) | 28.4501 | 19.9712
| 5 | Energy method (section. 2.3.3) | 10.6801 | 37.7412

## ST-135 linear charact. curve
Steam Turbine-135, mode with MP and LP steams
* Розовым подсвечены дополнительные вычисления, необходимые для поиска коэффициентов.
| Qп (MW) | Qт (MW) | N (MW) | Q0 (MW) | N^2 | Qп^2 | Qт^2 | N * Qп | N * Qт | Qп * Qт | Q0 * N | Q0 * Qп | Q0 * Qт | Q0'(MW) | MAPE | 1) Полагаем, что турбина описывается плоскостью:
Сумма * | 34958.649 | 23451.227 | 29846.6701 | 110709.249 | 3664464.42 | 6458916.2831 | 2209335.0623 | 4523091.9385 | 2792468.7555 | 3229582.9516 | 13651995.1538 | 17235573.0928 | 10338733.2899 |  | 0.1897% | Q0 = a1 * N + a2 * Qп + a3 * Qт + a0
точка №1 | 0 | 86.9019 | 61.4142 | 235.2182 | 3771.704 | 0 | 7551.9402 | 0 | 5337.0107 | 0 | 14445.7352 | 0 | 20440.9051 | 233.758 | 0.6208% | 2) Требуется найти коэффициенты a3, a2, a1 и a0 на основании приведенных точек
точка №2 | 0 | 86.9019 | 71.6437 | 254.2836 | 5132.8197 | 0 | 7551.9402 | 0 | 6225.9737 | 0 | 18217.8213 | 0 | 22097.7321 | 252.6742 | 0.6329% | Здесь 250 - число в ячейки (4,4) - соответствует количеству рассматриваемых точек
точка №3 | 0 | 86.9019 | 81.8732 | 273.3488 | 6703.2209 | 0 | 7551.9402 | 0 | 7114.9366 | 0 | 22379.9378 | 0 | 23754.5267 | 271.5903 | 0.6433%
точка №4 | 0 | 86.9019 | 92.1028 | 292.3732 | 8482.9166 | 0 | 7551.9402 | 0 | 8003.904 | 0 | 26928.3776 | 0 | 25407.7883 | 290.5066 | 0.6384% | 1) Zx | 3664464.42 | 4523091.9385 | 2792468.7555 | 29846.6701
точка №5 | 0 | 86.9019 | 102.3323 | 311.3975 | 10471.8996 | 0 | 7551.9402 | 0 | 8892.8713 | 0 | 31866.0218 | 0 | 27061.0339 | 309.4229 | 0.6341% |  | 4523091.9385 | 6458916.2831 | 3229582.9516 | 34958.649
точка №6 | 0 | 91.6131 | 64.56 | 242.4731 | 4167.9936 | 0 | 8392.9693 | 0 | 5914.545 | 0 | 15654.0624 | 0 | 22213.7231 | 240.9036 | 0.6473% |  | 2792468.7555 | 3229582.9516 | 2209335.0623 | 23451.227
точка №7 | 0 | 91.6131 | 73.844 | 259.7738 | 5452.9363 | 0 | 8392.9693 | 0 | 6765.0814 | 0 | 19182.737 | 0 | 23798.6968 | 258.0714 | 0.6553% |  | 29846.6701 | 34958.649 | 23451.227 | 250
точка №8 | 0 | 91.6131 | 83.128 | 277.0572 | 6910.2644 | 0 | 8392.9693 | 0 | 7615.6179 | 0 | 23031.2096 | 0 | 25382.0814 | 275.2392 | 0.6562%
точка №9 | 0 | 91.6131 | 92.412 | 294.227 | 8539.9777 | 0 | 8392.9693 | 0 | 8466.1544 | 0 | 27190.1065 | 0 | 26955.0632 | 292.407 | 0.6186% | 2) Zy | 13651995.1538
точка №10 | 0 | 91.6131 | 101.696 | 311.3968 | 10342.0764 | 0 | 8392.9693 | 0 | 9316.6909 | 0 | 31667.8126 | 0 | 28528.045 | 309.5747 | 0.5851% |  | 17235573.0928
точка №11 | 0 | 96.3244 | 67.943 | 250.1683 | 4616.2512 | 0 | 9278.39 | 0 | 6544.5687 | 0 | 16997.188 | 0 | 24097.3159 | 248.4879 | 0.6717% |  | 10338733.2899
точка №12 | 0 | 96.3244 | 74.9223 | 263.1726 | 5613.3585 | 0 | 9278.39 | 0 | 7216.8504 | 0 | 19717.5133 | 0 | 25349.9475 | 261.394 | 0.6759% |  | 110709.249
точка №13 | 0 | 96.3244 | 81.9017 | 276.1768 | 6707.8885 | 0 | 9278.39 | 0 | 7889.1321 | 0 | 22619.3466 | 0 | 26602.5612 | 274.3 | 0.6795%
точка №14 | 0 | 96.3244 | 91.5004 | 293.8295 | 8372.3232 | 0 | 9278.39 | 0 | 8813.7211 | 0 | 26885.514 | 0 | 28302.9474 | 292.0497 | 0.6057% | 3) Обр. Zx | 4.6292e-05 | -1.0999e-05 | -2.2014e-05 | -0.0019237
точка №15 | 0 | 96.3244 | 101.0991 | 311.482 | 10221.028 | 0 | 9278.39 | 0 | 9738.3101 | 0 | 31490.5487 | 0 | 30003.3157 | 309.7994 | 0.5402% |  | -1.0999e-05 | 3.3764e-06 | 9.2262e-06 | -2.4508e-05
точка №16 | 0 | 101.0357 | 71.4286 | 257.8583 | 5102.0449 | 0 | 10208.2026 | 0 | 7216.835 | 0 | 18418.4601 | 0 | 26052.8848 | 256.2619 | 0.6191% |  | -2.2014e-05 | 9.2262e-06 | 0.00013671 | -0.011486
точка №17 | 0 | 101.0357 | 78.7013 | 271.316 | 6193.8868 | 0 | 10208.2026 | 0 | 7951.6319 | 0 | 21352.9091 | 0 | 27412.5893 | 269.7103 | 0.5918% |  | -0.0019237 | -2.4508e-05 | -0.011486 | 1.3145
точка №18 | 0 | 101.0357 | 85.9739 | 284.7242 | 7391.5115 | 0 | 10208.2026 | 0 | 8686.4289 | 0 | 24478.854 | 0 | 28767.2995 | 283.1587 | 0.5498%
точка №19 | 0 | 101.0357 | 93.2465 | 298.0818 | 8694.9191 | 0 | 10208.2026 | 0 | 9421.2258 | 0 | 27795.1 | 0 | 30116.889 | 296.6072 | 0.4947% | 4) A | 1.8492 | = a1
точка №20 | 0 | 101.0357 | 100.5192 | 311.4369 | 10104.1096 | 0 | 10208.2026 | 0 | 10156.0227 | 0 | 31305.3872 | 0 | 31466.2288 | 310.0556 | 0.4435% |  | 0.71464 | = a2
точка №21 | 0 | 105.7469 | 74.9156 | 265.4616 | 5612.3471 | 0 | 11182.4069 | 0 | 7922.0925 | 0 | 19887.2181 | 0 | 28071.7456 | 264.0385 | 0.5361% |  | 0.28198 | = a3
точка №22 | 0 | 105.7469 | 81.1047 | 276.8351 | 6577.9805 | 0 | 11182.4069 | 0 | 8576.5759 | 0 | 22452.6432 | 0 | 29274.4557 | 275.4833 | 0.4883% |  | 95.6873 | = a0
точка №23 | 0 | 105.7469 | 87.2939 | 288.2084 | 7620.225 | 0 | 11182.4069 | 0 | 9231.0593 | 0 | 25158.8365 | 0 | 30477.1464 | 286.9282 | 0.4442% |  | Использование полученных
точка №24 | 0 | 105.7469 | 93.6175 | 299.8034 | 8764.2363 | 0 | 11182.4069 | 0 | 9899.7604 | 0 | 28066.8473 | 0 | 31703.2829 | 298.6216 | 0.3942% |  | кэффициентов продемонстировано в
точка №25 | 0 | 105.7469 | 99.9411 | 311.3984 | 9988.2235 | 0 | 11182.4069 | 0 | 10568.4615 | 0 | 31121.5024 | 0 | 32929.4195 | 310.3151 | 0.3479% |  | примере №2 (Exmp.2)
точка №26 | 34.89 | 86.9019 | 72.0316 | 278.7038 | 5188.5514 | 1217.3121 | 7551.9402 | 2513.1825 | 6259.6829 | 3032.0073 | 20075.4817 | 9723.9761 | 24219.891 | 278.3252 | 0.1359%
точка №27 | 34.89 | 86.9019 | 81.6363 | 296.375 | 6664.4936 | 1217.3121 | 7551.9402 | 2848.2923 | 7094.3539 | 3032.0073 | 24194.9752 | 10340.5246 | 25755.5527 | 296.0861 | 0.0975%
точка №28 | 34.89 | 86.9019 | 91.2411 | 314.046 | 8324.9383 | 1217.3121 | 7551.9402 | 3183.402 | 7929.0249 | 3032.0073 | 28653.9071 | 10957.0667 | 27291.1984 | 313.847 | 0.0634%
точка №29 | 34.89 | 86.9019 | 100.8471 | 331.6761 | 10170.1376 | 1217.3121 | 7551.9402 | 3518.5553 | 8763.8046 | 3032.0073 | 33448.5732 | 11572.1793 | 28823.2836 | 331.6102 | 0.01988%
точка №30 | 34.89 | 86.9019 | 110.4531 | 349.3062 | 12199.8873 | 1217.3121 | 7551.9402 | 3853.7087 | 9598.5843 | 3032.0073 | 38581.9481 | 12187.2919 | 30355.3689 | 349.3734 | 0.01924%
точка №31 | 34.89 | 91.6131 | 75.2393 | 285.9518 | 5660.9523 | 1217.3121 | 8392.9693 | 2625.0992 | 6892.9093 | 3196.3828 | 21514.8096 | 9976.8566 | 26196.9407 | 285.5853 | 0.1282%
точка №32 | 34.89 | 91.6131 | 83.8702 | 301.8083 | 7034.2063 | 1217.3121 | 8392.9693 | 2926.2304 | 7683.6109 | 3196.3828 | 25312.7137 | 10530.0911 | 27649.6077 | 301.5453 | 0.08714%
точка №33 | 34.89 | 91.6131 | 92.501 | 317.66 | 8556.4443 | 1217.3121 | 8392.9693 | 3227.3616 | 8474.3126 | 3196.3828 | 29383.8881 | 11083.1591 | 29101.8378 | 317.5053 | 0.04871%
точка №34 | 34.89 | 91.6131 | 101.1319 | 333.4834 | 10227.6663 | 1217.3121 | 8392.9693 | 3528.4929 | 9265.0142 | 3196.3828 | 33725.8198 | 11635.2364 | 30551.4662 | 333.4653 | 0.005418%
точка №35 | 34.89 | 91.6131 | 109.7628 | 349.307 | 12047.8723 | 1217.3121 | 8392.9693 | 3829.6241 | 10055.7159 | 3196.3828 | 38340.9106 | 12187.32 | 32001.1114 | 349.4254 | 0.0339%
точка №36 | 34.89 | 96.3244 | 78.5223 | 293.3208 | 6165.7516 | 1217.3121 | 9278.39 | 2739.643 | 7563.6134 | 3360.7583 | 23032.2264 | 10233.9639 | 28253.9532 | 292.9846 | 0.1146%
точка №37 | 34.89 | 96.3244 | 84.8965 | 305.0145 | 7207.4157 | 1217.3121 | 9278.39 | 2962.0389 | 8177.6044 | 3360.7583 | 25894.6645 | 10641.9563 | 29380.3399 | 304.7716 | 0.07963%
точка №38 | 34.89 | 96.3244 | 91.2707 | 316.7082 | 8330.3407 | 1217.3121 | 9278.39 | 3184.4347 | 8791.5954 | 3360.7583 | 28906.1783 | 11049.9488 | 30506.7265 | 316.5587 | 0.04721%
точка №39 | 34.89 | 96.3244 | 100.1684 | 333.0035 | 10033.6983 | 1217.3121 | 9278.39 | 3494.8737 | 9648.6562 | 3360.7583 | 33356.4083 | 11618.4911 | 32076.3596 | 333.012 | 0.002566%
точка №40 | 34.89 | 96.3244 | 109.066 | 349.2986 | 11895.3924 | 1217.3121 | 9278.39 | 3805.3127 | 10505.717 | 3360.7583 | 38096.5977 | 12187.0271 | 33645.9751 | 349.4654 | 0.04775%
точка №41 | 34.89 | 101.0357 | 81.8371 | 300.7755 | 6697.3109 | 1217.3121 | 10208.2026 | 2855.2964 | 8268.4646 | 3525.1338 | 24614.594 | 10494.0569 | 30389.0473 | 300.4428 | 0.1106%
точка №42 | 34.89 | 101.0357 | 88.4694 | 312.9257 | 7826.8392 | 1217.3121 | 10208.2026 | 3086.6982 | 8938.5659 | 3525.1338 | 27684.3545 | 10917.9768 | 31616.6489 | 312.7071 | 0.06985%
точка №43 | 34.89 | 101.0357 | 95.1018 | 325.0695 | 9044.3429 | 1217.3121 | 10208.2026 | 3318.1001 | 9608.6671 | 3525.1338 | 30914.678 | 11341.6747 | 32843.6079 | 324.9715 | 0.03016%
точка №44 | 34.89 | 101.0357 | 101.7341 | 337.1865 | 10349.822 | 1217.3121 | 10208.2026 | 3549.5019 | 10278.7684 | 3525.1338 | 34303.3581 | 11764.4375 | 34067.8586 | 337.2358 | 0.01462%
точка №45 | 34.89 | 101.0357 | 108.3664 | 349.2984 | 11743.2766 | 1217.3121 | 10208.2026 | 3780.9037 | 10948.8697 | 3525.1338 | 37852.2076 | 12187.0203 | 35291.5885 | 349.5002 | 0.05777%
точка №46 | 34.89 | 105.7469 | 85.1455 | 308.2013 | 7249.7562 | 1217.3121 | 11182.4069 | 2970.7265 | 9003.8727 | 3689.5093 | 26241.9518 | 10753.1425 | 32591.3296 | 307.8891 | 0.1013%
точка №47 | 34.89 | 105.7469 | 90.7176 | 318.3946 | 8229.6829 | 1217.3121 | 11182.4069 | 3165.1371 | 9593.105 | 3689.5093 | 28883.996 | 11108.7884 | 33669.2443 | 318.1929 | 0.06336%
точка №48 | 34.89 | 105.7469 | 96.2897 | 328.588 | 9271.7063 | 1217.3121 | 11182.4069 | 3359.5476 | 10182.3373 | 3689.5093 | 31639.6369 | 11464.4342 | 34747.159 | 328.4967 | 0.02778%
точка №49 | 34.89 | 105.7469 | 101.9819 | 338.9534 | 10400.2977 | 1217.3121 | 11182.4069 | 3558.1467 | 10784.2645 | 3689.5093 | 34567.0915 | 11826.083 | 35843.2679 | 339.0225 | 0.02039%
точка №50 | 34.89 | 105.7469 | 107.674 | 349.3184 | 11593.6903 | 1217.3121 | 11182.4069 | 3756.7459 | 11386.1917 | 3689.5093 | 37612.5097 | 12187.7191 | 36939.3382 | 349.5483 | 0.06581%
точка №51 | 69.78 | 86.9019 | 82.0226 | 320.8501 | 6727.7069 | 4869.2484 | 7551.9402 | 5723.537 | 7127.9198 | 6064.0146 | 26316.9634 | 22388.9233 | 27882.4875 | 321.734 | 0.2755%
точка №52 | 69.78 | 86.9019 | 92.166 | 339.4005 | 8494.5808 | 4869.2484 | 7551.9402 | 6431.347 | 8009.4049 | 6064.0146 | 31281.2008 | 23683.3649 | 29494.5458 | 340.491 | 0.3213%
точка №53 | 69.78 | 86.9019 | 102.3095 | 357.9506 | 10467.2338 | 4869.2484 | 7551.9402 | 7139.1569 | 8890.8899 | 6064.0146 | 36621.7481 | 24977.7937 | 31106.5883 | 359.2481 | 0.3625%
точка №54 | 69.78 | 86.9019 | 112.4529 | 376.5271 | 12645.6547 | 4869.2484 | 7551.9402 | 7846.9634 | 9772.3707 | 6064.0146 | 42341.5652 | 26274.0616 | 32720.9211 | 378.005 | 0.3925%
точка №55 | 69.78 | 86.9019 | 122.5963 | 395.1032 | 15029.8528 | 4869.2484 | 7551.9402 | 8554.7698 | 10653.8514 | 6064.0146 | 48438.1948 | 27570.3038 | 34335.2219 | 396.762 | 0.4198%
точка №56 | 69.78 | 91.6131 | 85.2627 | 328.0774 | 7269.728 | 4869.2484 | 8392.9693 | 5949.6312 | 7811.1845 | 6392.7656 | 27972.7666 | 22893.2424 | 30056.2059 | 329.054 | 0.2977%
точка №57 | 69.78 | 91.6131 | 94.4037 | 344.7827 | 8912.0633 | 4869.2484 | 8392.9693 | 6587.4919 | 8648.6226 | 6392.7656 | 32548.7714 | 24058.937 | 31586.6294 | 345.9574 | 0.3407%
точка №58 | 69.78 | 91.6131 | 103.5447 | 361.5016 | 10721.5153 | 4869.2484 | 8392.9693 | 7225.3527 | 9486.0607 | 6392.7656 | 37431.5936 | 25225.5822 | 33118.301 | 362.8608 | 0.376%
точка №59 | 69.78 | 91.6131 | 112.6858 | 378.3084 | 12698.0839 | 4869.2484 | 8392.9693 | 7863.2134 | 10323.4988 | 6392.7656 | 42629.9766 | 26398.361 | 34658.0253 | 379.7642 | 0.3848%
точка №60 | 69.78 | 91.6131 | 121.8268 | 395.1152 | 14841.7692 | 4869.2484 | 8392.9693 | 8501.0741 | 11160.9369 | 6392.7656 | 48135.6224 | 27571.1398 | 36197.7495 | 396.6676 | 0.3929%
точка №61 | 69.78 | 96.3244 | 88.5561 | 335.3934 | 7842.1828 | 4869.2484 | 9278.39 | 6179.4447 | 8530.1132 | 6721.5166 | 29701.1301 | 23403.7504 | 32306.5666 | 336.4726 | 0.3218%
точка №62 | 69.78 | 96.3244 | 95.447 | 347.978 | 9110.1394 | 4869.2484 | 9278.39 | 6660.2951 | 9193.8798 | 6721.5166 | 33213.4699 | 24281.9022 | 33518.7684 | 349.2152 | 0.3555%
точка №63 | 69.78 | 96.3244 | 102.338 | 360.5624 | 10473.0662 | 4869.2484 | 9278.39 | 7141.1456 | 9857.6464 | 6721.5166 | 36899.2303 | 25160.0412 | 34730.9526 | 361.9578 | 0.387%
точка №64 | 69.78 | 96.3244 | 111.7054 | 377.8535 | 12478.1076 | 4869.2484 | 9278.39 | 7794.8063 | 10759.9604 | 6721.5166 | 42208.2958 | 26366.6176 | 36396.5121 | 379.2799 | 0.3775%
точка №65 | 69.78 | 96.3244 | 121.0729 | 395.1445 | 14658.6471 | 4869.2484 | 9278.39 | 8448.467 | 11662.2744 | 6721.5166 | 47841.2869 | 27573.1811 | 38062.054 | 396.6019 | 0.3688%
точка №66 | 69.78 | 101.0357 | 91.8732 | 342.8752 | 8440.6849 | 4869.2484 | 10208.2026 | 6410.9119 | 9282.4685 | 7050.2677 | 31501.0429 | 23925.8322 | 34642.6198 | 343.935 | 0.3091%
точка №67 | 69.78 | 101.0357 | 98.9865 | 355.8987 | 9798.3272 | 4869.2484 | 10208.2026 | 6907.278 | 10001.1654 | 7050.2677 | 35229.1673 | 24834.6117 | 35958.4571 | 357.0887 | 0.3344%
точка №68 | 69.78 | 101.0357 | 106.0998 | 368.9593 | 11257.1676 | 4869.2484 | 10208.2026 | 7403.644 | 10719.8623 | 7050.2677 | 39146.509 | 25745.9807 | 37278.0437 | 370.2425 | 0.3478%
точка №69 | 69.78 | 101.0357 | 113.2131 | 382.0384 | 12817.206 | 4869.2484 | 10208.2026 | 7900.0101 | 11438.5591 | 7050.2677 | 43251.7469 | 26658.6367 | 38599.4939 | 383.3963 | 0.3554%
точка №70 | 69.78 | 101.0357 | 120.3264 | 395.115 | 14478.4425 | 4869.2484 | 10208.2026 | 8396.3762 | 12157.256 | 7050.2677 | 47542.7666 | 27571.1253 | 39920.7017 | 396.55 | 0.3632%
точка №71 | 69.78 | 105.7469 | 95.193 | 350.3927 | 9061.7072 | 4869.2484 | 11182.4069 | 6642.5675 | 10066.3647 | 7379.0187 | 33354.9343 | 24450.4041 | 37052.9441 | 351.4024 | 0.2882%
точка №72 | 69.78 | 105.7469 | 101.2302 | 361.474 | 10247.5433 | 4869.2484 | 11182.4069 | 7063.8399 | 10704.7745 | 7379.0187 | 36592.0656 | 25223.6546 | 38224.7532 | 362.5661 | 0.3021%
точка №73 | 69.78 | 105.7469 | 107.2673 | 372.5551 | 11506.2736 | 4869.2484 | 11182.4069 | 7485.1122 | 11343.1844 | 7379.0187 | 39962.9757 | 25996.8923 | 39396.543 | 373.7299 | 0.3154%
точка №74 | 69.78 | 105.7469 | 113.4286 | 383.8347 | 12866.0473 | 4869.2484 | 11182.4069 | 7915.0477 | 11994.7228 | 7379.0187 | 43537.8361 | 26783.9875 | 40589.3329 | 385.1233 | 0.3357%
точка №75 | 69.78 | 105.7469 | 119.5899 | 395.1148 | 14301.7442 | 4869.2484 | 11182.4069 | 8344.9832 | 12646.2612 | 7379.0187 | 47251.7354 | 27571.1084 | 41782.1617 | 396.5166 | 0.3548%
точка №76 | 104.67 | 86.9019 | 92.1756 | 364.0781 | 8496.3412 | 10955.8089 | 7551.9402 | 9648.0201 | 8010.2348 | 9096.0219 | 33559.1154 | 38108.0525 | 31639.0768 | 365.4424 | 0.3747%
точка №77 | 104.67 | 86.9019 | 102.1305 | 382.4177 | 10430.6492 | 10955.8089 | 7551.9402 | 10690.0047 | 8875.3388 | 9096.0219 | 39056.5342 | 40027.6649 | 33232.8283 | 383.8509 | 0.3748%
точка №78 | 104.67 | 86.9019 | 112.0855 | 400.7572 | 12563.1593 | 10955.8089 | 7551.9402 | 11731.9893 | 9740.4429 | 9096.0219 | 44919.073 | 41947.2579 | 34826.5636 | 402.2594 | 0.3748%
точка №79 | 104.67 | 86.9019 | 122.0405 | 419.0327 | 14893.8836 | 10955.8089 | 7551.9402 | 12773.9791 | 10605.5513 | 9096.0219 | 51138.9633 | 43860.1553 | 36414.74 | 420.6679 | 0.3902%
точка №80 | 104.67 | 86.9019 | 131.9955 | 437.3082 | 17422.812 | 10955.8089 | 7551.9402 | 13815.969 | 11470.6597 | 9096.0219 | 57722.7186 | 45773.0526 | 38002.9162 | 439.0765 | 0.4044%
точка №81 | 104.67 | 91.6131 | 95.6433 | 371.6037 | 9147.6408 | 10955.8089 | 8392.9693 | 10010.9842 | 8762.184 | 9589.1484 | 35541.4029 | 38895.7579 | 34043.7843 | 373.1833 | 0.4251%
точка №82 | 104.67 | 91.6131 | 104.5224 | 388.0531 | 10924.9321 | 10955.8089 | 8392.9693 | 10940.3596 | 9575.6263 | 9589.1484 | 40560.2446 | 40617.5212 | 35550.7697 | 389.6023 | 0.3992%
точка №83 | 104.67 | 91.6131 | 113.4015 | 404.4969 | 12859.9002 | 10955.8089 | 8392.9693 | 11869.735 | 10389.0686 | 9589.1484 | 45870.555 | 42338.6903 | 37057.235 | 406.0214 | 0.3769%
точка №84 | 104.67 | 91.6131 | 122.2806 | 420.9078 | 14952.5451 | 10955.8089 | 8392.9693 | 12799.1104 | 11202.5109 | 9589.1484 | 51468.8614 | 44056.4221 | 38560.6917 | 422.4404 | 0.3641%
точка №85 | 104.67 | 91.6131 | 131.1597 | 437.3186 | 17202.8669 | 10955.8089 | 8392.9693 | 13728.4858 | 12015.9533 | 9589.1484 | 57358.5723 | 45774.1346 | 40064.1317 | 438.8594 | 0.3523%
точка №86 | 104.67 | 96.3244 | 99.2047 | 379.3756 | 9841.5725 | 10955.8089 | 9278.39 | 10383.7559 | 9555.8332 | 10082.2749 | 37635.8436 | 39709.2451 | 36543.128 | 381.0974 | 0.4539%
точка №87 | 104.67 | 96.3244 | 105.6601 | 391.4017 | 11164.0567 | 10955.8089 | 9278.39 | 11059.4427 | 10177.6457 | 10082.2749 | 41355.5416 | 40968.0148 | 37701.5328 | 393.0346 | 0.4172%
точка №88 | 104.67 | 96.3244 | 112.1155 | 403.4278 | 12569.8853 | 10955.8089 | 9278.39 | 11735.1294 | 10799.4583 | 10082.2749 | 45230.5059 | 42226.7844 | 38859.9377 | 404.9718 | 0.3827%
точка №89 | 104.67 | 96.3244 | 121.2542 | 420.4323 | 14702.5931 | 10955.8089 | 9278.39 | 12691.6823 | 11679.7429 | 10082.2749 | 50979.2043 | 44006.6497 | 40497.8899 | 421.871 | 0.3422%
точка №90 | 104.67 | 96.3244 | 130.393 | 437.437 | 17002.3344 | 10955.8089 | 9278.39 | 13648.2353 | 12560.0275 | 10082.2749 | 57038.7274 | 45786.5345 | 42135.86 | 438.7702 | 0.3048%
точка №91 | 104.67 | 101.0357 | 102.8065 | 387.2856 | 10569.1764 | 10955.8089 | 10208.2026 | 10760.7564 | 10387.1216 | 10575.4015 | 39815.4803 | 40537.187 | 39129.6555 | 389.0863 | 0.4649%
точка №92 | 104.67 | 101.0357 | 109.5189 | 399.8304 | 11994.3895 | 10955.8089 | 10208.2026 | 11463.3433 | 11065.3132 | 10575.4015 | 43788.9828 | 41850.2453 | 40397.1217 | 401.4987 | 0.4173%
точка №93 | 104.67 | 101.0357 | 116.2313 | 412.3705 | 13509.7151 | 10955.8089 | 10208.2026 | 12165.9302 | 11743.5049 | 10575.4015 | 47930.3623 | 43162.8229 | 41664.1241 | 413.9112 | 0.3736%
точка №94 | 104.67 | 101.0357 | 122.9437 | 424.8824 | 15115.1534 | 10955.8089 | 10208.2026 | 12868.5171 | 12421.6966 | 10575.4015 | 52236.6158 | 44472.4421 | 42928.2707 | 426.3236 | 0.3392%
точка №95 | 104.67 | 101.0357 | 129.6561 | 437.3878 | 16810.7043 | 10955.8089 | 10208.2026 | 13571.104 | 13099.8883 | 10575.4015 | 56709.9935 | 45781.3787 | 44191.7584 | 438.736 | 0.3082%
точка №96 | 104.67 | 105.7469 | 106.4026 | 395.2278 | 11321.5133 | 10955.8089 | 11182.4069 | 11137.1601 | 11251.7451 | 11068.528 | 42053.2624 | 41368.4908 | 41794.1116 | 397.0646 | 0.4648%
точка №97 | 104.67 | 105.7469 | 111.9677 | 405.6614 | 12536.7658 | 10955.8089 | 11182.4069 | 11719.6592 | 11840.2372 | 11068.528 | 45420.9744 | 42460.5792 | 42897.4359 | 407.3555 | 0.4176%
точка №98 | 104.67 | 105.7469 | 117.5328 | 416.095 | 13813.9591 | 10955.8089 | 11182.4069 | 12302.1582 | 12428.7292 | 11068.528 | 48904.8148 | 43552.6675 | 44000.7603 | 417.6463 | 0.3728%
точка №99 | 104.67 | 105.7469 | 123.2228 | 426.7091 | 15183.8708 | 10955.8089 | 11182.4069 | 12897.7357 | 13030.4344 | 11068.528 | 52580.31 | 44663.6403 | 45123.1633 | 428.1683 | 0.342%
точка №100 | 104.67 | 105.7469 | 128.9129 | 437.3233 | 16618.5358 | 10955.8089 | 11182.4069 | 13493.3132 | 13632.1395 | 11068.528 | 56376.6182 | 45774.6325 | 46245.586 | 438.6902 | 0.3126%
точка №101 | 139.56 | 86.9019 | 103.6032 | 409.8421 | 10733.6231 | 19476.9936 | 7551.9402 | 14458.8626 | 9003.3149 | 12128.0292 | 42460.949 | 57197.5581 | 35616.0538 | 411.5078 | 0.4064%
точка №102 | 139.56 | 86.9019 | 113.3662 | 428.268 | 12851.884 | 19476.9936 | 7551.9402 | 15821.3799 | 9851.7338 | 12128.0292 | 48551.0975 | 59769.086 | 37217.3053 | 429.5612 | 0.302%
точка №103 | 139.56 | 86.9019 | 123.1291 | 446.6938 | 15160.7753 | 19476.9936 | 7551.9402 | 17183.8972 | 10700.1527 | 12128.0292 | 55001.0062 | 62340.5875 | 38818.5404 | 447.6146 | 0.2061%
точка №104 | 139.56 | 86.9019 | 132.8983 | 464.9982 | 17661.9714 | 19476.9936 | 7551.9402 | 18547.2937 | 11549.1191 | 12128.0292 | 61797.4996 | 64895.1552 | 40409.2311 | 465.6797 | 0.1466%
точка №105 | 139.56 | 86.9019 | 142.6676 | 483.3025 | 20354.0441 | 19476.9936 | 7551.9402 | 19910.6903 | 12398.0855 | 12128.0292 | 68951.6073 | 67449.6964 | 41999.9052 | 483.7448 | 0.09152%
точка №106 | 139.56 | 91.6131 | 106.953 | 417.4695 | 11438.9442 | 19476.9936 | 8392.9693 | 14926.3607 | 9798.3012 | 12785.5312 | 44649.6135 | 58262.0409 | 38245.6943 | 419.0306 | 0.374%
точка №107 | 139.56 | 91.6131 | 115.6719 | 433.9393 | 13379.9769 | 19476.9936 | 8392.9693 | 16143.1634 | 10597.0625 | 12785.5312 | 50194.5612 | 60560.5682 | 39754.5458 | 435.1533 | 0.2798%
точка №108 | 139.56 | 91.6131 | 124.3907 | 450.4073 | 15473.0462 | 19476.9936 | 8392.9693 | 17359.9661 | 11395.8239 | 12785.5312 | 56026.4753 | 62858.8383 | 41263.2286 | 451.276 | 0.1929%
точка №109 | 139.56 | 91.6131 | 133.1095 | 466.8669 | 17718.1523 | 19476.9936 | 8392.9693 | 18576.7688 | 12194.5852 | 12785.5312 | 62144.4377 | 65155.939 | 42771.1437 | 467.3988 | 0.1139%
точка №110 | 139.56 | 91.6131 | 141.8284 | 483.3266 | 20115.295 | 19476.9936 | 8392.9693 | 19793.5715 | 12993.3465 | 12785.5312 | 68549.4441 | 67453.066 | 44279.076 | 483.5215 | 0.04031%
точка №111 | 139.56 | 96.3244 | 110.3304 | 425.1602 | 12172.7972 | 19476.9936 | 9278.39 | 15397.7106 | 10627.5096 | 13443.0333 | 46908.0898 | 59335.351 | 40953.2966 | 426.6045 | 0.3397%
точка №112 | 139.56 | 96.3244 | 116.7475 | 437.2927 | 13629.9904 | 19476.9936 | 9278.39 | 16293.2881 | 11245.6377 | 13443.0333 | 51052.8523 | 61028.5703 | 42121.9577 | 438.471 | 0.2694%
точка №113 | 139.56 | 96.3244 | 123.1647 | 449.4251 | 15169.5433 | 19476.9936 | 9278.39 | 17188.8655 | 11863.7658 | 13443.0333 | 55353.3044 | 62721.7633 | 43290.6006 | 450.3374 | 0.203%
точка №114 | 139.56 | 96.3244 | 132.0762 | 466.3746 | 17444.1226 | 19476.9936 | 9278.39 | 18432.5545 | 12722.1607 | 13443.0333 | 61596.9878 | 65087.2421 | 44923.2556 | 466.8164 | 0.09473%
точка №115 | 139.56 | 96.3244 | 140.9877 | 483.3242 | 19877.5316 | 19476.9936 | 9278.39 | 19676.2434 | 13580.5556 | 13443.0333 | 68142.7629 | 67452.721 | 46555.9106 | 483.2954 | 0.005962%
точка №116 | 139.56 | 101.0357 | 113.7209 | 433.073 | 12932.4431 | 19476.9936 | 10208.2026 | 15870.8888 | 11489.8651 | 14100.5353 | 49249.449 | 60439.665 | 43755.81 | 434.2027 | 0.2609%
точка №117 | 139.56 | 101.0357 | 120.3273 | 445.6168 | 14478.6591 | 19476.9936 | 10208.2026 | 16792.878 | 12157.347 | 14100.5353 | 53619.8613 | 62190.2747 | 45023.1788 | 446.4191 | 0.18%
точка №118 | 139.56 | 101.0357 | 126.9337 | 458.1819 | 16112.1642 | 19476.9936 | 10208.2026 | 17714.8672 | 12824.8289 | 14100.5353 | 58158.7282 | 63943.8708 | 46292.7096 | 458.6355 | 0.09899%
точка №119 | 139.56 | 101.0357 | 133.5401 | 470.7611 | 17832.9583 | 19476.9936 | 10208.2026 | 18636.8564 | 13492.3108 | 14100.5353 | 62865.4784 | 65699.4128 | 47563.6492 | 470.8519 | 0.0193%
точка №120 | 139.56 | 101.0357 | 140.1465 | 483.3395 | 19641.0415 | 19476.9936 | 10208.2026 | 19558.8455 | 14159.7927 | 14100.5353 | 67738.3369 | 67454.8583 | 48834.5189 | 483.0683 | 0.0561%
точка №121 | 139.56 | 105.7469 | 117.1091 | 441.0364 | 13714.5413 | 19476.9936 | 11182.4069 | 16343.746 | 12383.9243 | 14758.0374 | 51649.3701 | 61551.0331 | 46638.2269 | 441.7965 | 0.1724%
точка №122 | 139.56 | 105.7469 | 122.6004 | 451.5075 | 15030.8703 | 19476.9936 | 11182.4069 | 17110.1188 | 12964.6175 | 14758.0374 | 55355.026 | 63012.3905 | 47745.5213 | 451.951 | 0.09823%
точка №123 | 139.56 | 105.7469 | 128.0918 | 461.9785 | 16407.5092 | 19476.9936 | 11182.4069 | 17876.4916 | 13545.3108 | 14758.0374 | 59175.6592 | 64473.7212 | 48852.7956 | 462.1055 | 0.02749%
точка №124 | 139.56 | 105.7469 | 133.6966 | 472.6611 | 17874.7675 | 19476.9936 | 11182.4069 | 18658.6905 | 14137.9957 | 14758.0374 | 63193.1549 | 65964.5795 | 49982.4433 | 472.4697 | 0.04049%
точка №125 | 139.56 | 105.7469 | 139.3013 | 483.3434 | 19404.8522 | 19476.9936 | 11182.4069 | 19440.8894 | 14730.6806 | 14758.0374 | 67330.3703 | 67455.4112 | 51112.071 | 482.8339 | 0.1054%
точка №126 | 174.45 | 86.9019 | 114.6862 | 456.0735 | 13152.9245 | 30432.8025 | 7551.9402 | 20007.0076 | 9966.4487 | 15160.0365 | 52305.3329 | 79562.0163 | 39633.6508 | 456.9359 | 0.1891%
точка №127 | 174.45 | 86.9019 | 123.6637 | 473.4381 | 15292.7107 | 30432.8025 | 7551.9402 | 21573.1325 | 10746.6105 | 15160.0365 | 58547.1114 | 82591.2825 | 41142.6734 | 473.5369 | 0.02086%
точка №128 | 174.45 | 86.9019 | 132.6412 | 490.8026 | 17593.6879 | 30432.8025 | 7551.9402 | 23139.2573 | 11526.7723 | 15160.0365 | 65100.6472 | 85620.5154 | 42651.6794 | 490.1379 | 0.1354%
точка №129 | 174.45 | 86.9019 | 141.5714 | 507.8422 | 20042.4755 | 30432.8025 | 7551.9402 | 24697.1395 | 12302.828 | 15160.0365 | 71895.961 | 88593.0772 | 44132.4548 | 506.6515 | 0.2345%
точка №130 | 174.45 | 86.9019 | 150.5017 | 524.8817 | 22650.7617 | 30432.8025 | 7551.9402 | 26255.0216 | 13078.8837 | 15160.0365 | 78995.5823 | 91565.6058 | 45613.2136 | 523.1651 | 0.327%
точка №131 | 174.45 | 91.6175 | 118.0055 | 463.9221 | 13925.298 | 30432.8025 | 8393.7663 | 20586.0595 | 10811.3689 | 15982.6729 | 54745.3562 | 80931.2057 | 42503.3805 | 464.4036 | 0.1038%
точка №132 | 174.45 | 91.6175 | 125.9685 | 479.2271 | 15868.0693 | 30432.8025 | 8393.7663 | 21975.2092 | 11540.9213 | 15982.6729 | 60367.5343 | 83601.1723 | 43905.5913 | 479.1286 | 0.02055%
точка №133 | 174.45 | 91.6175 | 133.9315 | 494.5139 | 17937.6601 | 30432.8025 | 8393.7663 | 23364.3589 | 12270.4738 | 15982.6729 | 66231.0197 | 86267.9584 | 45306.1317 | 493.8537 | 0.1335%
точка №134 | 174.45 | 91.6175 | 141.8946 | 509.7086 | 20134.0704 | 30432.8025 | 8393.7663 | 24753.5086 | 13000.0262 | 15982.6729 | 72324.8791 | 88918.6577 | 46698.2237 | 508.5788 | 0.2217%
точка №135 | 174.45 | 91.6175 | 149.8576 | 524.9032 | 22457.3003 | 30432.8025 | 8393.7663 | 26142.6583 | 13729.5787 | 15982.6729 | 78660.7285 | 91569.3571 | 48090.3157 | 523.3038 | 0.3047%
точка №136 | 174.45 | 96.3331 | 121.2854 | 471.6144 | 14710.1483 | 30432.8025 | 9280.0662 | 21158.238 | 11683.7986 | 16805.3093 | 57199.9368 | 82273.1258 | 45432.0737 | 471.7984 | 0.03903%
точка №137 | 174.45 | 96.3331 | 126.9552 | 482.4418 | 16117.6228 | 30432.8025 | 9280.0662 | 22147.3346 | 12229.988 | 16805.3093 | 61248.4958 | 84161.9728 | 46475.1146 | 482.2829 | 0.03294%
точка №138 | 174.45 | 96.3331 | 132.625 | 493.2696 | 17589.3906 | 30432.8025 | 9280.0662 | 23136.4313 | 12776.1774 | 16805.3093 | 65419.8847 | 86050.8869 | 47518.1926 | 492.7674 | 0.1018%
точка №139 | 174.45 | 96.3331 | 140.8114 | 508.891 | 19827.8363 | 30432.8025 | 9280.0662 | 24564.54 | 13564.7939 | 16805.3093 | 71657.6298 | 88776.0363 | 49023.0483 | 507.9054 | 0.1937%
точка №140 | 174.45 | 96.3331 | 148.9977 | 524.5126 | 22200.3146 | 30432.8025 | 9280.0662 | 25992.6488 | 14353.4103 | 16805.3093 | 78151.1675 | 91501.2189 | 50527.9224 | 523.0434 | 0.2801%
точка №141 | 174.45 | 101.04 | 124.5417 | 479.6869 | 15510.635 | 30432.8025 | 10209.0816 | 21726.2996 | 12583.6934 | 17626.428 | 59741.0168 | 83681.3725 | 48467.5602 | 479.1472 | 0.1125%
точка №142 | 174.45 | 101.04 | 130.4184 | 490.9928 | 17008.9525 | 30432.8025 | 10209.0816 | 22751.4855 | 13177.4726 | 17626.428 | 64034.4782 | 85653.6874 | 49609.9087 | 490.0142 | 0.1993%
точка №143 | 174.45 | 101.04 | 136.2951 | 502.2962 | 18576.3407 | 30432.8025 | 10209.0816 | 23776.6715 | 13771.2519 | 17626.428 | 68460.481 | 87625.5661 | 50752.0045 | 500.8812 | 0.2817%
точка №144 | 174.45 | 101.04 | 142.1717 | 513.5188 | 20212.7994 | 30432.8025 | 10209.0816 | 24801.8574 | 14365.0311 | 17626.428 | 73007.8465 | 89583.346 | 51885.9345 | 511.7482 | 0.3448%
точка №145 | 174.45 | 101.04 | 148.0484 | 524.7243 | 21918.3287 | 30432.8025 | 10209.0816 | 25827.0434 | 14958.8103 | 17626.428 | 77684.5982 | 91538.1602 | 53018.1468 | 522.6153 | 0.4019%
точка №146 | 174.45 | 105.7469 | 127.7968 | 487.8492 | 16332.0221 | 30432.8025 | 11182.4069 | 22294.1518 | 13514.1154 | 18447.5467 | 62345.5666 | 85105.2929 | 51588.5405 | 486.4937 | 0.2779%
точка №147 | 174.45 | 105.7469 | 132.5711 | 497.1021 | 17575.0833 | 30432.8025 | 11182.4069 | 23127.0197 | 14018.9776 | 18447.5467 | 65901.3496 | 86719.4643 | 52567.0078 | 495.3221 | 0.3581%
точка №148 | 174.45 | 105.7469 | 137.3453 | 506.355 | 18863.7314 | 30432.8025 | 11182.4069 | 23959.8876 | 14523.8397 | 18447.5467 | 69545.4841 | 88333.6357 | 53545.4751 | 504.1506 | 0.4354%
точка №149 | 174.45 | 105.7469 | 142.2201 | 515.6433 | 20226.5711 | 30432.8025 | 11182.4069 | 24810.3052 | 15039.34 | 18447.5467 | 73334.8709 | 89953.9779 | 54527.683 | 513.165 | 0.4806%
точка №150 | 174.45 | 105.7469 | 147.095 | 524.9314 | 21636.939 | 30432.8025 | 11182.4069 | 25660.7228 | 15554.8403 | 18447.5467 | 77214.7877 | 91574.2868 | 55509.8707 | 522.1795 | 0.5242%
точка №151 | 218.7086 | 87.0096 | 130.6752 | 518.1735 | 17076.0079 | 47833.4537 | 7570.6705 | 28579.7907 | 11369.9969 | 19029.7482 | 67712.4238 | 113328.9998 | 45086.0676 | 518.1616 | 0.002289%
точка №152 | 218.7086 | 87.0096 | 131.9597 | 520.6339 | 17413.3756 | 47833.4537 | 7570.6705 | 28860.7328 | 11481.7651 | 19029.7482 | 68702.7162 | 113867.1086 | 45300.1453 | 520.537 | 0.01861%
точка №153 | 218.7086 | 87.0096 | 133.2443 | 523.0945 | 17754.0435 | 47833.4537 | 7570.6705 | 29141.6749 | 11593.5332 | 19029.7482 | 69699.3551 | 114405.2593 | 45514.2397 | 522.9123 | 0.03481%
точка №154 | 218.7086 | 87.0096 | 134.5289 | 525.5676 | 18098.0115 | 47833.4537 | 7570.6705 | 29422.6171 | 11705.3014 | 19029.7482 | 70704.0026 | 114946.1529 | 45729.4252 | 525.2877 | 0.05325%
точка №155 | 218.7086 | 87.0096 | 135.8134 | 528.0407 | 18445.2796 | 47833.4537 | 7570.6705 | 29703.5592 | 11817.0696 | 19029.7482 | 71715.0039 | 115487.0465 | 45944.6108 | 527.6631 | 0.07152%
точка №156 | 218.7086 | 88.5172 | 131.7319 | 520.601 | 17353.2935 | 47833.4537 | 7835.2947 | 28810.9 | 11660.5389 | 19359.4733 | 68579.7552 | 113859.9122 | 46082.1404 | 520.5408 | 0.01156%
точка №157 | 218.7086 | 88.5172 | 132.703 | 522.4571 | 17610.0995 | 47833.4537 | 7835.2947 | 29023.2989 | 11746.5024 | 19359.4733 | 69331.6533 | 114265.8677 | 46246.4414 | 522.3366 | 0.02307%
точка №158 | 218.7086 | 88.5172 | 133.6742 | 524.3144 | 17868.7917 | 47833.4537 | 7835.2947 | 29235.6978 | 11832.4659 | 19359.4733 | 70087.3033 | 114672.0633 | 46410.8395 | 524.1324 | 0.0347%
точка №159 | 218.7086 | 88.5172 | 134.6454 | 526.1717 | 18129.3703 | 47833.4537 | 7835.2947 | 29448.0966 | 11918.4294 | 19359.4733 | 70846.5775 | 115078.2861 | 46575.2488 | 525.9283 | 0.04627%
точка №160 | 218.7086 | 88.5172 | 135.6165 | 528.0289 | 18391.8351 | 47833.4537 | 7835.2947 | 29660.4955 | 12004.3929 | 19359.4733 | 71609.4332 | 115484.4669 | 46739.641 | 527.7241 | 0.05773%
точка №161 | 218.7086 | 90.0248 | 132.8009 | 523.0431 | 17636.079 | 47833.4537 | 8104.4646 | 29044.6995 | 11955.3745 | 19689.1984 | 69460.6008 | 114394.0371 | 47086.8548 | 522.9427 | 0.01921%
точка №162 | 218.7086 | 90.0248 | 133.362 | 524.1133 | 17785.423 | 47833.4537 | 8104.4646 | 29167.4169 | 12005.8874 | 19689.1984 | 69896.8044 | 114628.0992 | 47183.1994 | 523.9802 | 0.0254%
точка №163 | 218.7086 | 90.0248 | 133.8764 | 525.0905 | 17922.8905 | 47833.4537 | 8104.4646 | 29279.9206 | 12052.1961 | 19689.1984 | 70297.2323 | 114841.8211 | 47271.1716 | 524.9314 | 0.0303%
точка №164 | 218.7086 | 90.0248 | 134.3908 | 526.0677 | 18060.8871 | 47833.4537 | 8104.4646 | 29392.4243 | 12098.5049 | 19689.1984 | 70698.6655 | 115055.5431 | 47359.1438 | 525.8827 | 0.03518%
точка №165 | 218.7086 | 90.0248 | 135.4196 | 528.0221 | 18338.4681 | 47833.4537 | 8104.4646 | 29617.4318 | 12191.1224 | 19689.1984 | 71504.5479 | 115482.987 | 47535.0882 | 527.7851 | 0.04489%
точка №166 | 218.7086 | 91.5324 | 133.8699 | 525.4851 | 17921.1501 | 47833.4537 | 8378.1802 | 29278.499 | 12253.4332 | 20018.9235 | 70346.6347 | 114928.1079 | 48098.9102 | 525.3445 | 0.02674%
точка №167 | 218.7086 | 91.5324 | 134.2081 | 526.1285 | 18011.8074 | 47833.4537 | 8378.1802 | 29352.4608 | 12284.3872 | 20018.9235 | 70610.6968 | 115068.836 | 48157.8068 | 525.9699 | 0.03015%
точка №168 | 218.7086 | 91.5324 | 134.5462 | 526.7718 | 18102.6934 | 47833.4537 | 8378.1802 | 29426.4226 | 12315.3412 | 20018.9235 | 70875.1686 | 115209.5225 | 48216.6859 | 526.5952 | 0.03352%
точка №169 | 218.7086 | 91.5324 | 134.8844 | 527.415 | 18193.8081 | 47833.4537 | 8378.1802 | 29500.3844 | 12346.2951 | 20018.9235 | 71140.0755 | 115350.2092 | 48275.5651 | 527.2206 | 0.03687%
точка №170 | 218.7086 | 91.5324 | 135.2226 | 528.0569 | 18285.1516 | 47833.4537 | 8378.1802 | 29574.3462 | 12377.2491 | 20018.9235 | 71405.2277 | 115490.589 | 48334.3159 | 527.8459 | 0.03995%
точка №171 | 218.7086 | 93.04 | 134.9389 | 527.9285 | 18208.5067 | 47833.4537 | 8656.4416 | 29512.2985 | 12554.7153 | 20348.6486 | 71238.0923 | 115462.5076 | 49118.4685 | 527.7464 | 0.03449%
точка №172 | 218.7086 | 93.04 | 134.9606 | 527.9699 | 18214.3636 | 47833.4537 | 8656.4416 | 29517.0445 | 12556.7342 | 20348.6486 | 71255.1288 | 115471.5509 | 49122.3156 | 527.7866 | 0.03472%
точка №173 | 218.7086 | 93.04 | 134.9823 | 528.0114 | 18220.2213 | 47833.4537 | 8656.4416 | 29521.7905 | 12558.7532 | 20348.6486 | 71272.1927 | 115480.6358 | 49126.1803 | 527.8267 | 0.03498%
точка №174 | 218.7086 | 93.04 | 135.004 | 528.0525 | 18226.08 | 47833.4537 | 8656.4416 | 29526.5365 | 12560.7722 | 20348.6486 | 71289.194 | 115489.6161 | 49130.0006 | 527.8668 | 0.03516%
точка №175 | 218.7086 | 93.04 | 135.0257 | 528.0935 | 18231.9397 | 47833.4537 | 8656.4416 | 29531.2824 | 12562.7911 | 20348.6486 | 71306.1969 | 115498.5965 | 49133.8209 | 527.9069 | 0.03533%
точка №176 | 218.7355 | 87.0096 | 130.6874 | 518.2155 | 17079.1965 | 47845.2313 | 7570.6705 | 28585.9775 | 11371.0584 | 19032.0908 | 67724.2378 | 113352.1435 | 45089.7243 | 518.2034 | 0.002333%
точка №177 | 218.7355 | 87.0096 | 131.9665 | 520.6657 | 17415.1571 | 47845.2313 | 7570.6705 | 28865.7621 | 11482.3524 | 19032.0908 | 68710.427 | 113888.0817 | 45302.9122 | 520.5687 | 0.01862%
точка №178 | 218.7355 | 87.0096 | 133.2456 | 523.1158 | 17754.3899 | 47845.2313 | 7570.6705 | 29145.5467 | 11593.6464 | 19032.0908 | 69702.8842 | 114424.0199 | 45516.1002 | 522.934 | 0.03476%
точка №179 | 218.7355 | 87.0096 | 134.5247 | 525.5784 | 18096.8949 | 47845.2313 | 7570.6705 | 29425.3313 | 11704.9403 | 19032.0908 | 70703.2779 | 114962.6711 | 45730.3672 | 525.2993 | 0.05311%
точка №180 | 218.7355 | 87.0096 | 135.8038 | 528.0408 | 18442.6721 | 47845.2313 | 7570.6705 | 29705.1159 | 11816.2343 | 19032.0908 | 71709.9452 | 115501.2801 | 45944.6175 | 527.6646 | 0.07125%
точка №181 | 218.7355 | 88.5172 | 131.7441 | 520.6433 | 17356.5079 | 47845.2313 | 7835.2947 | 28817.1153 | 11661.6188 | 19361.8565 | 68591.6828 | 113883.1869 | 46085.887 | 520.5826 | 0.01166%
точка №182 | 218.7355 | 88.5172 | 132.7098 | 522.4895 | 17611.8844 | 47845.2313 | 7835.2947 | 29028.3427 | 11747.0977 | 19361.8565 | 69339.4635 | 114287.016 | 46249.3073 | 522.3683 | 0.0232%
точка №183 | 218.7355 | 88.5172 | 133.6755 | 524.3363 | 17869.1259 | 47845.2313 | 7835.2947 | 29239.5701 | 11832.5765 | 19361.8565 | 70090.8882 | 114690.9732 | 46412.7794 | 524.154 | 0.03477%
точка №184 | 218.7355 | 88.5172 | 134.6411 | 526.1827 | 18128.2325 | 47845.2313 | 7835.2947 | 29450.7976 | 11918.0554 | 19361.8565 | 70845.8339 | 115094.8559 | 46576.2214 | 525.9397 | 0.04619%
точка №185 | 218.7355 | 88.5172 | 135.6068 | 528.0292 | 18389.2042 | 47845.2313 | 7835.2947 | 29662.025 | 12003.5342 | 19361.8565 | 71604.3452 | 115498.7381 | 46739.6631 | 527.7254 | 0.05753%
точка №186 | 218.7355 | 90.0248 | 132.8131 | 523.0866 | 17639.3195 | 47845.2313 | 8104.4646 | 29050.9436 | 11956.4728 | 19691.6222 | 69472.7575 | 114417.6313 | 47090.7697 | 522.9845 | 0.01953%
точка №187 | 218.7355 | 90.0248 | 133.3648 | 524.1395 | 17786.1699 | 47845.2313 | 8104.4646 | 29171.62 | 12006.1394 | 19691.6222 | 69901.7595 | 114647.9302 | 47185.5536 | 524.0046 | 0.02573%
точка №188 | 218.7355 | 90.0248 | 133.8761 | 525.1104 | 17922.8035 | 47845.2313 | 8104.4646 | 29283.454 | 12052.1669 | 19691.6222 | 70299.7247 | 114860.3095 | 47272.9624 | 524.9501 | 0.03054%
точка №189 | 218.7355 | 90.0248 | 134.3873 | 526.0814 | 18059.9598 | 47845.2313 | 8104.4646 | 29395.288 | 12098.1943 | 19691.6222 | 70698.6827 | 115072.6887 | 47360.3711 | 525.8955 | 0.03533%
точка №190 | 218.7355 | 90.0248 | 135.4099 | 528.0231 | 18335.841 | 47845.2313 | 8104.4646 | 29618.956 | 12190.2492 | 19691.6222 | 71499.5513 | 115497.4054 | 47535.1714 | 527.7864 | 0.04482%
точка №191 | 218.7355 | 91.5324 | 133.8821 | 525.5275 | 17924.4167 | 47845.2313 | 8378.1802 | 29284.7718 | 12254.5499 | 20021.3879 | 70358.7219 | 114951.5296 | 48102.791 | 525.3863 | 0.02685%
точка №192 | 218.7355 | 91.5324 | 134.2148 | 526.1604 | 18013.6192 | 47845.2313 | 8378.1802 | 29357.5506 | 12285.005 | 20021.3879 | 70618.5274 | 115089.9753 | 48160.7252 | 526.0016 | 0.03018%
точка №193 | 218.7355 | 91.5324 | 134.5476 | 526.7935 | 18103.0432 | 47845.2313 | 8378.1802 | 29430.3294 | 12315.4602 | 20021.3879 | 70878.7798 | 115228.4626 | 48218.6768 | 526.6169 | 0.03353%
точка №194 | 218.7355 | 91.5324 | 134.8803 | 527.4263 | 18192.6886 | 47845.2313 | 8378.1802 | 29503.1082 | 12345.9153 | 20021.3879 | 71139.4022 | 115366.8667 | 48276.5936 | 527.2321 | 0.03681%
точка №195 | 218.7355 | 91.5324 | 135.213 | 528.0581 | 18282.5554 | 47845.2313 | 8378.1802 | 29575.887 | 12376.3704 | 20021.3879 | 71400.3136 | 115505.0572 | 48334.421 | 527.8474 | 0.03989%
точка №196 | 218.7355 | 93.04 | 134.9511 | 527.9705 | 18211.7994 | 47845.2313 | 8656.4416 | 29518.6001 | 12555.8503 | 20351.1535 | 71250.2005 | 115485.9073 | 49122.3758 | 527.7882 | 0.03452%
точка №197 | 218.7355 | 93.04 | 134.9674 | 528.0016 | 18216.1856 | 47845.2313 | 8656.4416 | 29522.1546 | 12557.3622 | 20351.1535 | 71262.9729 | 115492.7026 | 49125.2662 | 527.8183 | 0.03471%
точка №198 | 218.7355 | 93.04 | 134.9836 | 528.0324 | 18220.5723 | 47845.2313 | 8656.4416 | 29525.709 | 12558.8741 | 20351.1535 | 71275.7206 | 115499.4561 | 49128.1388 | 527.8483 | 0.03487%
точка №199 | 218.7355 | 93.04 | 134.9998 | 528.0631 | 18224.9595 | 47845.2313 | 8656.4416 | 29529.2635 | 12560.386 | 20351.1535 | 71288.4434 | 115506.1677 | 49130.9937 | 527.8784 | 0.03499%
точка №200 | 218.7355 | 93.04 | 135.0161 | 528.094 | 18229.3473 | 47845.2313 | 8656.4416 | 29532.8179 | 12561.8979 | 20351.1535 | 71301.1928 | 115512.9207 | 49133.8661 | 527.9084 | 0.03514%
точка №201 | 218.7625 | 87.0096 | 130.6874 | 518.2344 | 17079.1965 | 47857.0102 | 7570.6705 | 28589.496 | 11371.0584 | 19034.4334 | 67726.7019 | 113370.2205 | 45091.3649 | 518.2227 | 0.002258%
точка №202 | 218.7625 | 87.0096 | 131.964 | 520.6799 | 17414.5105 | 47857.0102 | 7570.6705 | 28868.7791 | 11482.1392 | 19034.4334 | 68711.0236 | 113905.2035 | 45304.1467 | 520.5834 | 0.01852%
точка №203 | 218.7625 | 87.0096 | 133.2407 | 523.1254 | 17753.0841 | 47857.0102 | 7570.6705 | 29148.0622 | 11593.22 | 19034.4334 | 69701.5893 | 114440.1865 | 45516.9284 | 522.9442 | 0.03464%
точка №204 | 218.7625 | 87.0096 | 134.5174 | 525.5831 | 18094.9309 | 47857.0102 | 7570.6705 | 29427.3562 | 11704.3052 | 19034.4334 | 70700.0734 | 114977.8496 | 45730.7762 | 525.305 | 0.05291%
точка №205 | 218.7625 | 87.0096 | 135.7941 | 528.0409 | 18440.0376 | 47857.0102 | 7570.6705 | 29706.6502 | 11815.3903 | 19034.4334 | 71704.8332 | 115515.5127 | 45944.6239 | 527.6659 | 0.07102%
точка №206 | 218.7625 | 88.5172 | 131.7563 | 520.6856 | 17359.7226 | 47857.0102 | 7835.2947 | 28823.3312 | 11662.6988 | 19364.2397 | 68603.602 | 113906.4482 | 46089.6273 | 520.6244 | 0.01175%
точка №207 | 218.7625 | 88.5172 | 132.7165 | 522.5217 | 17613.676 | 47857.0102 | 7835.2947 | 29033.3924 | 11747.6952 | 19364.2397 | 69347.2635 | 114308.1268 | 46252.1573 | 522.4 | 0.02329%
точка №208 | 218.7625 | 88.5172 | 133.6767 | 524.3583 | 17869.4735 | 47857.0102 | 7835.2947 | 29243.4535 | 11832.6916 | 19364.2397 | 70094.5091 | 114709.9002 | 46414.7257 | 524.1756 | 0.03483%
точка №209 | 218.7625 | 88.5172 | 134.637 | 526.1939 | 18127.115 | 47857.0102 | 7835.2947 | 29453.5147 | 11917.688 | 19364.2397 | 70845.1535 | 115111.4652 | 46577.2097 | 525.9512 | 0.04611%
точка №210 | 218.7625 | 88.5172 | 135.5972 | 528.0295 | 18386.6006 | 47857.0102 | 7835.2947 | 29663.5759 | 12002.6845 | 19364.2397 | 71599.3231 | 115513.0302 | 46739.6938 | 527.7269 | 0.05731%
точка №211 | 218.7625 | 90.0248 | 132.8254 | 523.1298 | 17642.5869 | 47857.0102 | 8104.4646 | 29057.2101 | 11957.5801 | 19694.0459 | 69484.9281 | 114441.1627 | 47094.6578 | 523.0264 | 0.01976%
точка №212 | 218.7625 | 90.0248 | 133.3661 | 524.162 | 17786.5166 | 47857.0102 | 8104.4646 | 29175.495 | 12006.2565 | 19694.0459 | 69905.4453 | 114666.97 | 47187.5816 | 524.0263 | 0.0259%
точка №213 | 218.7625 | 90.0248 | 133.8746 | 525.1273 | 17922.4219 | 47857.0102 | 8104.4646 | 29286.7466 | 12052.0386 | 19694.0459 | 70301.2375 | 114878.1421 | 47274.4829 | 524.9667 | 0.03059%
точка №214 | 218.7625 | 90.0248 | 134.3832 | 526.0928 | 18058.8444 | 47857.0102 | 8104.4646 | 29397.9983 | 12097.8207 | 19694.0459 | 70698.0371 | 115089.3557 | 47361.4012 | 525.9071 | 0.0353%
точка №215 | 218.7625 | 90.0248 | 135.4003 | 528.0236 | 18333.2412 | 47857.0102 | 8104.4646 | 29620.5016 | 12189.3849 | 19694.0459 | 71494.5565 | 115511.7415 | 47535.2207 | 527.7879 | 0.04464%
точка №216 | 218.7625 | 91.5324 | 133.8944 | 525.57 | 17927.7104 | 47857.0102 | 8378.1802 | 29291.0672 | 12255.6758 | 20023.8522 | 70370.8786 | 114974.9797 | 48106.6826 | 525.4283 | 0.02695%
точка №217 | 218.7625 | 91.5324 | 134.2216 | 526.1926 | 18015.4446 | 47857.0102 | 8378.1802 | 29362.6517 | 12285.6275 | 20023.8522 | 70626.423 | 115111.1786 | 48163.6696 | 526.0334 | 0.03025%
точка №218 | 218.7625 | 91.5324 | 134.5489 | 526.815 | 18103.393 | 47857.0102 | 8378.1802 | 29434.2363 | 12315.5792 | 20023.8522 | 70882.3493 | 115247.3359 | 48220.6392 | 526.6385 | 0.03349%
точка №219 | 218.7625 | 91.5324 | 134.8761 | 527.4374 | 18191.5556 | 47857.0102 | 8378.1802 | 29505.8208 | 12345.5308 | 20023.8522 | 71138.683 | 115383.4933 | 48277.6088 | 527.2436 | 0.03673%
точка №220 | 218.7625 | 91.5324 | 135.2033 | 528.0588 | 18279.9323 | 47857.0102 | 8378.1802 | 29577.4054 | 12375.4825 | 20023.8522 | 71395.2941 | 115519.4405 | 48334.4905 | 527.8487 | 0.03979%
точка №221 | 218.7625 | 93.04 | 134.9634 | 528.0126 | 18215.1193 | 47857.0102 | 8656.4416 | 29524.9243 | 12556.9947 | 20353.6585 | 71262.3807 | 115509.3389 | 49126.2957 | 527.8302 | 0.03455%
точка №222 | 218.7625 | 93.04 | 134.9742 | 528.0332 | 18218.0212 | 47857.0102 | 8656.4416 | 29527.2759 | 12557.9949 | 20353.6585 | 71270.8353 | 115513.8422 | 49128.211 | 527.8501 | 0.03468%
точка №223 | 218.7625 | 93.04 | 134.9849 | 528.0536 | 18220.9232 | 47857.0102 | 8656.4416 | 29529.6276 | 12558.9951 | 20353.6585 | 71279.2647 | 115518.3038 | 49130.1085 | 527.87 | 0.03478%
точка №224 | 218.7625 | 93.04 | 134.9957 | 528.0741 | 18223.8255 | 47857.0102 | 8656.4416 | 29531.9793 | 12559.9953 | 20353.6585 | 71287.7074 | 115522.7864 | 49132.015 | 527.8899 | 0.03489%
точка №225 | 218.7625 | 93.04 | 135.0064 | 528.0944 | 18226.728 | 47857.0102 | 8656.4416 | 29534.331 | 12560.9955 | 20353.6585 | 71296.1249 | 115527.2274 | 49133.9037 | 527.9097 | 0.03497%
точка №226 | 218.7894 | 87.0096 | 130.6996 | 518.2766 | 17082.3854 | 47868.7906 | 7570.6705 | 28595.6838 | 11372.1199 | 19036.776 | 67738.539 | 113393.4046 | 45095.0362 | 518.2645 | 0.002334%
точка №227 | 218.7894 | 87.0096 | 131.9708 | 520.7115 | 17416.2921 | 47868.7906 | 7570.6705 | 28873.8089 | 11482.7265 | 19036.776 | 68718.7168 | 113926.1496 | 45306.9017 | 520.6151 | 0.01851%
точка №228 | 218.7894 | 87.0096 | 133.242 | 523.1465 | 17753.4306 | 47868.7906 | 7570.6705 | 29151.9339 | 11593.3331 | 19036.776 | 69705.0853 | 114458.8947 | 45518.7673 | 522.9658 | 0.03454%
точка №229 | 218.7894 | 87.0096 | 134.5132 | 525.594 | 18093.8144 | 47868.7906 | 7570.6705 | 29430.0699 | 11703.9441 | 19036.776 | 70699.352 | 114994.3744 | 45731.7204 | 525.3166 | 0.05277%
точка №230 | 218.7894 | 87.0096 | 135.7845 | 528.0414 | 18437.4304 | 47868.7906 | 7570.6705 | 29708.2059 | 11814.555 | 19036.776 | 71699.8415 | 115529.8543 | 45944.6736 | 527.6674 | 0.07084%
точка №231 | 218.7894 | 88.5172 | 131.7686 | 520.7278 | 17362.9639 | 47868.7906 | 7835.2947 | 28829.5696 | 11663.7875 | 19366.6229 | 68615.5689 | 113929.7028 | 46093.364 | 520.6664 | 0.01179%
точка №232 | 218.7894 | 88.5172 | 132.7234 | 522.5537 | 17615.5142 | 47868.7906 | 7835.2947 | 29038.4807 | 11748.3082 | 19366.6229 | 69355.1338 | 114329.2039 | 46254.993 | 522.432 | 0.02329%
точка №233 | 218.7894 | 88.5172 | 133.6783 | 524.3801 | 17869.8879 | 47868.7906 | 7835.2947 | 29247.3917 | 11832.8288 | 19366.6229 | 70098.2361 | 114728.7874 | 46416.6554 | 524.1977 | 0.03477%
точка №234 | 218.7894 | 88.5172 | 134.6332 | 526.2057 | 18126.0851 | 47868.7906 | 7835.2947 | 29456.3027 | 11917.3495 | 19366.6229 | 70844.7317 | 115128.2175 | 46578.2557 | 525.9634 | 0.04604%
точка №235 | 218.7894 | 88.5172 | 135.588 | 528.031 | 18384.1057 | 47868.7906 | 7835.2947 | 29665.2138 | 12001.8701 | 19366.6229 | 71594.662 | 115527.564 | 46739.8222 | 527.7291 | 0.05717%
точка №236 | 218.7894 | 90.0248 | 132.8376 | 523.1724 | 17645.828 | 47868.7906 | 8104.4646 | 29063.4555 | 11958.6784 | 19696.4697 | 69496.9633 | 114464.558 | 47098.4889 | 523.0682 | 0.01991%
точка №237 | 218.7894 | 90.0248 | 133.3674 | 524.1839 | 17786.8634 | 47868.7906 | 8104.4646 | 29179.3701 | 12006.3735 | 19696.4697 | 69909.0487 | 114685.8758 | 47189.554 | 524.0479 | 0.02594%
точка №238 | 218.7894 | 90.0248 | 133.8736 | 525.1446 | 17922.1274 | 47868.7906 | 8104.4646 | 29290.1103 | 12051.9396 | 19696.4697 | 70302.9709 | 114896.0572 | 47276.0369 | 524.9839 | 0.0306%
точка №239 | 218.7894 | 90.0248 | 134.3797 | 526.1054 | 18057.9038 | 47868.7906 | 8104.4646 | 29400.8506 | 12097.5056 | 19696.4697 | 70697.8911 | 115106.2802 | 47362.5369 | 525.9199 | 0.03527%
точка №240 | 218.7894 | 90.0248 | 135.392 | 528.0269 | 18330.9937 | 47868.7906 | 8104.4646 | 29622.3311 | 12188.6377 | 19696.4697 | 71490.6237 | 115526.6846 | 47535.5198 | 527.7918 | 0.04454%
точка №241 | 218.7894 | 91.5324 | 133.9066 | 525.6122 | 17930.9775 | 47868.7906 | 8378.1802 | 29297.3413 | 12256.7925 | 20026.3166 | 70382.9362 | 114998.3543 | 48110.5418 | 525.4701 | 0.02702%
точка №242 | 218.7894 | 91.5324 | 134.2289 | 526.2254 | 18017.411 | 47868.7906 | 8378.1802 | 29367.8681 | 12286.2979 | 20026.3166 | 70634.6831 | 115132.5267 | 48166.6739 | 526.0662 | 0.03025%
точка №243 | 218.7894 | 91.5324 | 134.5513 | 526.8383 | 18104.0523 | 47868.7906 | 8378.1802 | 29438.3948 | 12315.8034 | 20026.3166 | 70886.7741 | 115266.6158 | 48222.7713 | 526.6623 | 0.0334%
точка №244 | 218.7894 | 91.5324 | 134.8736 | 527.4515 | 18190.9015 | 47868.7906 | 8378.1802 | 29508.9216 | 12345.3089 | 20026.3166 | 71139.3116 | 115400.7882 | 48278.9034 | 527.2584 | 0.03662%
точка №245 | 218.7894 | 91.5324 | 135.196 | 528.0648 | 18277.9584 | 47868.7906 | 8378.1802 | 29579.4483 | 12374.8144 | 20026.3166 | 71392.2443 | 115534.9605 | 48335.0356 | 527.8545 | 0.03983%
точка №246 | 218.7894 | 93.04 | 134.9756 | 528.0545 | 18218.4126 | 47868.7906 | 8656.4416 | 29531.2272 | 12558.1298 | 20356.1635 | 71274.4762 | 115532.7193 | 49130.1929 | 527.872 | 0.03456%
точка №247 | 218.7894 | 93.04 | 134.9817 | 528.0662 | 18220.0593 | 47868.7906 | 8656.4416 | 29532.5618 | 12558.6974 | 20356.1635 | 71279.2668 | 115535.2632 | 49131.2747 | 527.8833 | 0.03463%
точка №248 | 218.7894 | 93.04 | 134.9878 | 528.0778 | 18221.7061 | 47868.7906 | 8656.4416 | 29533.8964 | 12559.2649 | 20356.1635 | 71284.0576 | 115537.8071 | 49132.3565 | 527.8946 | 0.03469%
точка №249 | 218.7894 | 93.04 | 134.9939 | 528.0894 | 18223.353 | 47868.7906 | 8656.4416 | 29535.231 | 12559.8325 | 20356.1635 | 71288.8485 | 115540.3511 | 49133.4383 | 527.9059 | 0.03476%
точка №250 | 218.7894 | 93.04 | 135 | 528.101 | 18225 | 47868.7906 | 8656.4416 | 29536.5656 | 12560.4 | 20356.1635 | 71293.6395 | 115542.895 | 49134.5201 | 527.9171 | 0.03482%